## Sheet1
Spec | Service | Service_Abbv | Size | Pipe | Schedule | Coupling | Fitting | Joint | Valve | Flange | Bolts | Clamps | SOLDER | Gasket | Insulation | Support Spacing | Test Pressure | Flexible Hose | MAXIMUM PRESSURE (PSI) | MAXIMUM TEMPERATURE (F) | Thread Compound | Strainers | Traps | o'lets | 90 deg elbow | 45 deg elbow | Tee | Coatings | Lining | Unions
PIQ GR-01 | Chilled Water | CHW | < = 2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Press Fit | Press Fit | Johnson Controls VG1000/VG1245 Series: Popular forged brass, stainless steel trim.Max Pressure: Minimum 150 psi or 250 psi | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket | 8 ft | 225 psig |  | 150 psig | 125 deg F
PIQ GR-01 | Chilled Water | CHW | > 2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Victallic | Victaulic | 150# Butterfly valves (Lug or Wafer style) or OS&Y Gate valves. Double Regulating Valves (DRV) or Venturi Valves | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket |  | 225 psig |  | 150 psig | 125 deg F
PIQ CPVC- 03 | Industrial Water | IW | < = 2" | ASTM D2846 CPVC SDR 11 | Sch 80 | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED. CHECK VALVE 1/2 TO 2 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROLTHREADED OR SOLDER BRONZE BODY,STAINLESS STEEL DISC | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1/2" THICK FOR 1" AND SMALLER,1" FOR 1 1/2" AND LARGER,EXTERIOR: PROVIDE ALUMINUM JACKET,INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  | 150 psig | 125 deg F
PIQ CPVC -03 | Industrial Water | IW | > 2" | ASTM F441 CPVC | Sch 80 | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1" FOR 2" AND LARGER, EXTERIOR: PROVIDE ALUMINUM JACKET, INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  | 150 psig | 125 deg F
PIQ CS-04 | Steam 125# | Stm 125# | < = 2" | Carbon Steel , A106 Gr B | Sch 80 | For forged fittings (e.g., couplings, half-couplings, threaded/socket-welded tees, and unions), the governing material specification is ASTM A105. Dimensional standards depend on the connection type: [1, 2].Socket Weld: ASME B16.11. Threaded (NPT) ASME B1.20.1 | SW ,ASTM A-105 | SW | On/Off Gate CL150 Bronze Cast or Stainless Steel or Ball Steam Rated w/ reinforced TFE 9tEFLON) SEATS TO>350 DEG.F. Globe - Throttling Steam Rated. Check Valve-Bronze or Cast Iron Swing Check Valves with metallic seating, or specialized Silent (Spring-Loaded) Check Valves | 150# ,RF | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  |  | 2" Mineral wool w/ Alum.Jacket |  | 187.5 psig |  | 150 psig | 125 deg F
PIQ CS-04 | Steam 125# | Stm 125# | > 2" | Carbon Steel , A106 Gr B | Sch 40 or Std WT >=12" | Use BW | ASTM A234 | BW | On/Off Gate CL150 Bronze Cast or Stainless Steel or Ball Steam Rated w/ reinforced TFE 9tEFLON) SEATS TO>350 DEG.F. Globe - Throttling Steam Rated. Check Valve-Bronze or Cast Iron Swing Check Valves with metallic seating, or specialized Silent (Spring-Loaded) Check Valves | 150# ,RF | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  |  | 2" Mineral wool w/ Alum.Jacket |  | 187.5 psig |  | 150 psig | 125 deg F
PIQ AL-05 | Compress Air | CA | < = 2" | ASTM B241,ALUMINUM-ALLOY , SEAMLESS PIPE | Sch 10 | Fiber Glass-Reinforced Ployamide Body Push-To-Connect Socket | Fiber Glass-Reinforced Polyamide Body Push-To-Connect Socket | Fiber Glass-Reinforced Polyamide Body Push-To-Connect Socket | Ball Valve Fiberglass-Reinforced Polyamide Body Push To Connect Socket | [7 empty] | 150 psig |  | 150 psig | 125 deg F
PIQ AL -05 | Compress Air | CA | > 2" | ASTM B241,ALUMINUM-ALLOY , SEAMLESS PIPE | Sch 10 | Fiber Glass-Reinforced Ployamide Body Push-To-Connect Socket | Fiber Glass-Reinforced Polyamide Body Push-To-Connect Socket | Fiber Glass-Reinforced Polyamide Body Push-To-Connect Socket | Ball Valve Fiberglass-Reinforced Polyamide Body Push To Connect Socket | [7 empty] | 150psig |  | 150 psig | 125 deg F
PIQ TB-06 | DI | DI | < = 2" | Tubing SMLS or Welded ASTM-270 | OD | Tri- Clamps or Buttwelded | Ferrules w/ TC or TC x BE | Ferrules w/ TC or TC x BE | Sanitary ball valve, 150# forged 316L stainless steel body sanitary TC x TC. Poppet type check valve, 316L SS, sanitary clamp ends, PTFE TCxTC poppet and gasket. Internal finish 20 Ra max. PBM Model VC or HC or approved equal |  |  | Tri-Clamp, 2 piece heavy duty, 304 stainless steel material hand tightened wing nut type. Tri-Clover Type 13MHHM or approved |  | Molded one piece “O” Ring Gasket. For fractional fittings FDA approved. Tri-Clover 42 MP-E, or approved equal. |  |  | 187.5 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length | 150 psig | 125 deg F
PIQ TB -06 | DI | DI | > 2" | Tubing SMLS or Welded ASTM-270 | OD | Tri- Clamps or Buttwelded | Ferrules w/ TC or TC x BE | Ferrules w/ TC or TC x BE | Tri-clamp ends. Internal finish to be same as tubing (20Ra Max) meeting BPE surface designation SF1. Body to be standard satin finish on exterior. Valves to have TEF seats and seals, stainless steel ball and stem, lockable handle,PBM Igenix Series 8 valves or approved equal stainless steel nuts and bolts. |  |  | Tri-Clamp 2-piece, 304 S.S. high pressure, high temperature (For use above |  | Molded one piece “O” Ring Gasket, FDA approved. Tri-Clover Type 1, 40 MP-E, or equal |  |  | 187.5 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length | 150 psig | 125 deg F
PIQ CS-01 | COMPRESSED AIR | CA | < = 2" | THREADED: ANSI B36 STEEL.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK | Sch 80 | ANSI B16.39 CLASS 150, ASTM A197 IRON | THREADED: ANSI B16.3 CLASS 150, ASTM A197 IRON | ANSI B1.20.1 TAPER THREADED(3) | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-01 | COMPRESSED AIR | CA | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD, SOCKET WELD, OR FLANGED, THREADED CONNECTIONS NOT PERMITTED | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | l. |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-02 | Natural Gas | NG | < = 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | ANSI B16.11, ASTM A105 CLASS 3000 STEEL | ANSI B1.20.1 TAPER THREADED(4) | BALL ≤2 1000 PSI THREE PIECE, FULL PORT, BLOW-OFF PROOF STEMSOCKET WELD OR THREADED CARBON STEEL. CHECK 1/2 TO 2 1000 PSI CWP LIFT CHECK THREADED ALL BRONZE .EQUIPMENT SERVICE REGULATORS(1) GLOBE OR ANGLE ≤1 125 INLET, 2.2 MAX OUTLET DIRECT OPERATED, SPRING LOADED, INTERNAL RELIEF THREADED CAST IRON BODY, ALUMINUM ORIFICE, NITRILE O-RINGS NITRILE O-RINGS | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-02 | Natural Gas | NG | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL or SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | PLUG >2 200 CWP LUBRICATED FLANGED CAST IRON BODY, TEFLON COATED PLUG. | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-03 | NATURAL GAS HIGH PRESSURE | NG HP | < = 2" | 1/2'-3/4" ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 160 BLACK STEEL;or ASTM A106, SEAMLESS, GRADE B SCHEDULE 160 BLACK STEEL 1'-2" ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | 1/2"-1" SCH 160,1'-2" Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | ANSI B16.11, ASTM A105 CLASS 3000 | ANSI B1.20.1 TAPER THREADED(3,4) | ,ALL BRONZE. <=1" Pressure Regulator 125 INLET, 2.2 MAX OUTLET,DIRECT OPERATED, SPRING LOADED, INTERNAL RELIEF,THREADED,CAST IRON BODY, ALUMINUM ORIFICE, NITRILE O-RINGS | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, CARBON STEEL CENTERING RING FOR FLAT FACE FLANGES: ANSI B16.21, FULL FACE, 1/8-INCH THICK, PTFE WITH BARIUM SULFATE |  |  | 450 psig |  | 150 psig | 125 deg F
PIQ CS-03 | NATURAL GAS HIGH PRESSURE | NG HP | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL;or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | PLUG,200 CWP,LUBRICATED,FLANGED,CAST IRON BODY, TEFLON COATED PLUG | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, CARBON STEEL CENTERING RING FOR FLAT FACE FLANGES: ANSI B16.21, FULL FACE, 1/8-INCH THICK, PTFE WITH BARIUM SULFATE |  |  | 450 psig |  | 150 psig | 125 deg F
PIQ CS-04 | STEAM, LOW PRESSURE | STM LP | < = 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 STEE | Threaded ANSI B16.11, ASTM A105 CLASS 3000 STEE | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-04 | STEAM, LOW PRESSURE | STMLP | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, LOW PRESSURE: SPIRAL WOUND 150 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-05 | STEAM, MEDIUM PRESSURE | STM MP | < = 2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, LOW PRESSURE: SPIRAL WOUND 150 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 450 psig |  | PRESSURE (PSI)(1): 740 655 600 410 | MAXIMUM TEMPERATURE (F): 100 300 500 800
PIQ CS-05 | STEAM, MEDIUM PRESSURE | STM MP | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, MEDIUM PRESSURE: SPIRAL WOUND 300 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 450 psig |  | PRESSURE (PSI)(1): 740 655 600 410 | MAXIMUM TEMPERATURE (F): 100 300 500 800 MAXIMUMPRESSURE (PSI)(1): 740 655 600 410
PIQ CS-06 | STEAM, HIGH PRESSURE | STM HP | < = 2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3) | ANSI B16.11, ASTM A105 CLASS 3000 | ANSI B1.20.1 TAPER THREADED(3) | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, MEDIUM PRESSURE: SPIRAL WOUND 300 LB GASKET .SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800
PIQ CS-06 | STEAM, HIGH PRESSURE | STM HP | > 2" | ASTM A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, HIGH PRESSURE: SPIRAL WOUND 600 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800
PIQ CS-07 | CHEMICAL | CHEMICAL | < = 2" | 1"-4" THERMALOK STYLE: ASTM A5873 CARBON STEEL, SCHEDULE 40 DIMENSIONS, PTFE LINER and 6"-8" THERMALOK STYLE: ASTM A53, GRADE B CARBON STEEL , SCHEDULE 40 DIMENSIONS, PTFE LINER | Sch 40 | NOT AVAILABLE, USE FLANGED CONNECTIONS,AISI 15V24 STEEL (1"-2") OR ASTM A513 STEEL | ANSI B16.5 ASTM A216 GRADE WCB CAST STEEL, OR FABRICATED CARBON STEEL. | FLANGED | Plastic-Lined Plug or Ball Valves,Tight quarter-turn shutoff, Fully encapsulated bodies and internals where the ball or plug component is either solid plastic or heavily coated in a thick layer of PFA or PTFE, ensuring zero fluid-to-metal contact .Lined Check Valves Flanged Features a poppet-type design where every single surface making contact with the line media is covered with a thick protective layer of plastic to eliminate corrosion and fluid trapping | ROTATING FLANGES: ASTM A395 DUCTILE IRON OR ASTM A105 STEEL; ANSI B16.5 CLASS 150, ASTM A105 STEEL | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, HIGH PRESSURE: SPIRAL WOUND 600 LB GASKET. Verify with Engineer. Consider No Gasket LINER THEMALOK MECHANICALLY LOCKED ASTM F1545 PTFE. MINIMUM LINER FLANGE FACE THICKNESS: 0.1" |  |  | 225 psig |  | MAXIMUM PRESSURE (PSI)(1): 285 260 200 170 | MAXIMUM TEMPERATURE (F): -20 to 100 200 400 450
PIQ CS-07 | CHEMICAL | CHEMICAL | > 2" | 1"-4" -6"-8" SWAGED STYLE: ASTM A513 ERW C-1010 ALUMINUM KILLED CARBON STEEL WITH CHEMICAL COMPOSTION MEETING ASTM A587, SCHEDULE 40 DIMENSIONS, PTFE LINED DIAMOND PICKED SPIRAL GROOVED INTERIOR | Sch 40 | (3"-4"), TAPPED OR STANDARD VENTED COUPLER OVER BUTT WELDED LINER ,>4" NOT AVAILABLE, USE FLANGED CONNECTIONS | ANSI B16.5 ASTM A216 GRADE WCB CAST STEEL, OR FABRICATED CARBON STEEL. | Flanged or MECHANICALLY COUPLED WITH BUTT WELDED LINER AVAILABLE THROUGH 4". | Plastic-Lined Plug or Ball Valves,Tight quarter-turn shutoff, Fully encapsulated bodies and internals where the ball or plug component is either solid plastic or heavily coated in a thick layer of PFA or PTFE, ensuring zero fluid-to-metal contact .Lined Check Valves Flanged Features a poppet-type design where every single surface making contact with the line media is covered with a thick protective layer of plastic to eliminate corrosion and fluid trapping | SLIP-ON, WELD NECK AND SOCKET WELD FLANGES: ANSI B16.5 CLASS 150, ASTM A105 STEELANSI B16.5 CLASS 150, ASTM A105 STEEL, CHAMFERED THREADED FLANGE OR ROTATING FLANGE(5) | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | No Gasket -SWAGED MECHANICALLY LOCKED ASTM F1545 PTFE. MINIMUM LINER FLANGE FACE THICKNESS: 0.1" |  |  | 225 psig |  | MAXIMUM PRESSURE (PSI)(1): 285 260 200 170 | MAXIMUM TEMPERATURE (F): -20 to 100 200 400 450
PIQ CU-01-PW | POTABLE WATER | PW | < = 2" | 1/4"-2" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED) NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PW | POTABLE WATER | PW | > 2" | 2"&3" - ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-NP | NON-POTABLE WATER | NPW | < = 2" | 1/4"TO 2" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01 NP | NON-POTABLE WATER | NPW | > 2" | 3" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PA | PLANT AIR | PA | < = 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PA | PLANT AIR | PA | > 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ-CU -01 F0 | FUEL OIL | FO | < = 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED CODE/ASME B31.9 |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ-CU 01 FO | FUEL OIL | FO | > 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED CODE/ASME B31.9 |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
Spec | Service | Service | Size | Pipe | Schedule | Coupling | Fitting | Joint | Valve | Flange | Bolts | Clamps | SOLDER | Gasket | Insulation | Support Spacing | Test Pressure | Flexible Hose |  | MAXIMUM TEMPERATURE (F): MAXIMUM PRESSURE (PSI)(1): | Jacket/Armour
PIQ-CU-02 | AIR | AIR | < = 2" | Size: < = 1/2" ASTM B68 AND B75 SOFT ANNEALED, BIRGHT SEAMLESS |  |  | ASTM B75 SEAMLESS WROUGHT COPPER |  | BALL <3 600 PSI WOG TWO PIECE, FULL PORT, LEVER HANDLE THREADED OR SOLDER. BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY. CHECK VALVE 1/2 TO 2 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROLTHREADED OR SOLDER BRONZE BODY,STAINLESS STEEL DISC. PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. |  |  |  | SERVICE PRESSURE AND TEMPERATURE LIMITED BY ASME B31.9 AS INDICATED IN THE PIPE SCHEDULE |  |  |  | JACKET: ASTM D1047 PVC, FLAME RETARDANT ARMOR: FLEXIBLE, INTERLOCKING GALVANIZED STEEL
PIQ-CU-02 | INSTRUMENT AIR | IA | < = 2" | Size: < = 1/2" ASTM B68 AND B75 SOFT ANNEALED, BIRGHT SEAMLESS |  |  | ASTM B75 SEAMLESS WROUGHT COPPER |  | BALL <3 600 PSI WOG TWO PIECE, FULL PORT, LEVER HANDLE THREADED OR SOLDER. BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY. CHECK VALVE 1/2 TO 2 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROLTHREADED OR SOLDER BRONZE BODY,STAINLESS STEEL DISC. PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. |  |  |  | SERVICE PRESSURE AND TEMPERATURE LIMITED BY ASME B31.9 AS INDICATED IN THE PIPE SCHEDULE |  |  |  | JACKET: ASTM D1047 PVC, FLAME RETARDANT ARMOR: FLEXIBLE, INTERLOCKING GALVANIZED STEEL
PIQ CS-01 | HOT WATER | HW | < = 2" | THREADED: ANSI B36 STEEL.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK | Sch 80 | ANSI B16.39 CLASS 150, ASTM A197 IRON | THREADED: ANSI B16.3 CLASS 150, ASTM A197 IRON | ANSI B1.20.1 TAPER THREADED(3) | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CS-01 | HOT WATER | HW | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD, SOCKET WELD, OR FLANGED, THREADED CONNECTIONS NOT PERMITTED | Ball Valve 150# Flange RF CS API 608 / ISO 17292ASME B16.10,Check Valve,Swing 150# Flanged RF CS,API 594 / BS 1868ASME B16.10 | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | l. |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CS-01-FO | FUEL OIL | FO | < = 2" | THREADED: ANSI B36 STEEL.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK | Sch 80 | ANSI B16.39 CLASS 150, ASTM A197 IRON | THREADED: ANSI B16.3 CLASS 150, ASTM A197 IRON | ANSI B1.20.1 TAPER THREADED(3) | BALL 500 PSI WOG LEVEL OPERATED, DOUBLE SEAL, UL LISTED THREADED 316 SS BODY AND BALL, TEFLON SEATS. CHECK VALVE 250 PSI WOG Y-PATTERN SWING CHECK THREADED ALL IRON. PRESSURE RELIEF VALVE 150 PSI ADJUSTABLE, SPRING LOADED THREADED BRONZE BODY | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CS-01-FO | FUEL OIL | FO | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD, SOCKET WELD, OR FLANGED, THREADED CONNECTIONS NOT PERMITTED | Ball Valve 150# Flange RF CS API 608 / ISO 17292ASME B16.10,Check Valve,Swing 150# Flanged RF CS,API 594 / BS 1868ASME B16.10 | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | l. |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CPVC- 03 | Plant Water | PW | < = 2" | ASTM D2846 CPVC SDR 11 | Sch 80 | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1/2" THICK FOR 1" AND SMALLER,1" FOR 1 1/2" AND LARGER,EXTERIOR: PROVIDE ALUMINUM JACKET,INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  |  | 150 psig | 125 deg F
PIQ CPVC -03 | Plant Water | PW | > 2" | ASTM F441 CPVC | Sch 80 | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1" FOR 2" AND LARGER, EXTERIOR: PROVIDE ALUMINUM JACKET, INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  |  | 150 psig | 125 deg F
PIQ CA-01 | COMPRESSED AIR | CA | < = 2" | THREADED: ANSI B36 STEEL.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK | Sch 80 | ANSI B16.39 CLASS 150, ASTM A197 IRON | THREADED: ANSI B16.3 CLASS 150, ASTM A197 IRON | ANSI B1.20.1 TAPER THREADED(3) | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CA-01 | COMPRESSED AIR | CA | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD, SOCKET WELD, OR FLANGED, THREADED CONNECTIONS NOT PERMITTED | Ball Valve 150# Flange RF CS API 608 / ISO 17292ASME B16.10,Check Valve,Swing 150# Flanged RF CS,API 594 / BS 1868ASME B16.10 | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | l. |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ-SS-01 | Chemical | CHEMICAL | < = 2" | ANSI B36.19, ASTM A312 or A778, SCHEDULE 40 TYPE 304L STAINLESS STEEL | Sch 40 | ANSI B1.20.1 TAPER THREADED(3)<=100 DEG F BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITT>=200 DEG F | ANSI B16.11, CLASS 3000 ASTM A182 GRADE F304L STAINLESS STEEL <=100 DEG F | ANSI B1.20.1 TAPER THREADED(3)<=100 DEG F BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITT>=200 DEG F | Cast Stainless Valves: Governed by ASTM A351 / ASME SA351 | ANSI B16.5 CLASS 150, ASTM A182 GRADE F304L STAINLESS STEEL, RAISED FACE, SOCKET WELD @ -20 TO 200 DEG F | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK . @ -20 TO 200 DEG F. GASKET MATERIALS SHALL BE SELECTED BASED SERVICE: |  |  | 225 psig |  | 1/2"-2" Pipe 275 PSIG @ 200 DEG F, 2" to 12" Pipe 185 PSIG @ 250 DEG F, 175 PSIG @ 300 DEG F | 1/2" TO 2" Pipe 200 DEG F, 2" TO 12" Pipe 300 DEG F | PROVIDE TEFLON PASTE THREAD LUBRICANT AND SEAL OR TEFLON TAPE FOR THREADED JOINTS. |  |  | USE FITTINGS | [5 empty] | NSI B16.11, CLASS 3000 ASTM A182 GRADE F304L STAINLESS STEEL, SOCKET WELD OR THREADED
PIQ-SS-01 | Chemical | CHEMICAL | > 2" | ANSI B36.19, ASTM A312 or A778, SCHEDULE 40 TYPE 304L STAINLESS STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITT>=200 TO 300 DEG F | BUTT WELD: ANSI B16.9, ASTM A403 CLASS WP304L STAINLESS STEEL. SOCKET WELD: ANSI B16.11, CLASS 3000 ASTM A182 GRADE F304L STAINLESS STEEL .>=200 TO 300 DEG F | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITT>=200 TO 300 DEG F | Forged Stainless Valves: Governed by ASTM A182 / ASME SA182 | ANSI B16.5 CLASS 150, ASTM A182 GRADE F304L STAINLESS STEEL, RAISED FACE, SLIP ON OR WELD NECK. 250 TO 300 DEG F | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS |  |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK . 250 TO 300 DEG F. GASKET MATERIALS SHALL BE SELECTED BASED SERVICE: |  |  | 225 psig |  | 1/2"-2" Pipe 275 PSIG @ 200 DEG F, 2" to 12" Pipe 185 PSIG @ 250 DEG F, 175 PSIG @ 300 DEG F | 1/2" TO 2" Pipe 200 DEG F, 2" TO 12" Pipe 300 DEG F |  |  |  | FOR BRANCHES SAME SIZE OR ONE SIZE SMALLER THAN HEADER: USE FITTING FOR BRANCHES 2 OR MORE SIZES SMALLER THAN HEADER: ASTM A182, CLASS 3000, GRADE F304L STAINLESS STEEL THREADOLET OR WELDOLET | [5 empty] | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS
PIQ-FB-01 | Food & Beverage | F&B | < = 2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5 S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball or True Bore-Self Clean ,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
PIQ-FB-01 | Food & Beverage | F&B | > 2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball True Bore-Self Clean,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
PIQ-SW-01 | Sanitary Waste (Above Grrade) | SW | < = 2" | 1 1/2" (Only not <1 1/2")- Cast Iron (Hubless / No-Hub, CISPI 301, ASTM A888 or PVC Schedule 40 Solid Wall (ASTM D2665, ASTM D1785-Disadvantage: Rarely used above ground in commercial builds because large-diameter Note: PVC expands/contracts heavily with temperature changes and requires massive structural expansion joints. Many commercial plumbing engineers write their specs to allow PVC Schedule 40 for smaller branch lines (≤ 2") to save on labor and material costs, but strictly mandate Cast Iron for all lines larger than 2" (> 2") to control noise from toilets and handle heavy drainage volumes |  | Heavy-duty, 300-series stainless steel shield with multi-band clamps (e.g., Clamp-All 125 or Husky SD) or PVC Schedule 40 PVC DWV (drain, waste, and vent | Heavy-duty cast iron or ductile iron (ASTM A74, ASME B16.12) or PVC Schedule 40 PVC DWV (drain, waste, and vent | Heavy-duty cast iron or ductile iron (ASTM A74, ASME B16.12)
PIQ-SW-01 | Sanitary Waste (Above Grrade) | SW | < = 2" | >=1 1/2" Cast Iron (Hubless / No-Hub, CISPI 301, ASTM A888 or PVC Schedule 40 Solid Wall (ASTM D2665, ASTM D1785-Disadvantage: Rarely used above ground in commercial builds because large-diameter Many commercial plumbing engineers write their specs to allow PVC Schedule 40 for smaller branch lines (≤ 2") to save on labor and material costs, but strictly mandate Cast Iron for all lines larger than 2" (> 2") to control noise from toilets and handle heavy drainage volumes. |  | Heavy-duty, 300-series stainless steel shield with multi-band clamps (e.g., Clamp-All 125 or Husky SD) | Heavy-duty cast iron or ductile iron (ASTM A74, ASME B16.12) | Heavy-duty cast iron or ductile iron (ASTM A74, ASME B16.12)
Glycol
Nitrogen
Spec | Service | Service | Size | Pipe | Schedule | Coupling | Fitting | Joint | Valve | Flange | Bolts | Clamps |  | Gasket | Insulation | Support Spacing | Test Pressure | Flexible Hose |  | MAXIMUM TEMPERATURE (F): MAXIMUM PRESSURE (PSI)(1):
Carbon Dioxide
Oxygen
Argon
Helium
Hydrogen
Propane

## NewSpecs
Master Spec | Combined Services | Recommended Pipe/Material | Joint | Typical Use
PIQ CW-01 | Cooling Water; Cooling Water Supply; Cooling Water Return; Condenser Water | Carbon Steel ASTM A53/A106 Sch40 | Victaulic >2, Press-fit/BW/SW <=2 | Closed/open cooling water
PIQ TW-01 | Tower Water; Tower Water Supply; Tower Water Return | Carbon Steel ASTM A53 Sch40 HDG optional | Victaulic/BW | Cooling tower
PIQ GLY-01 | Glycol; Glycol Supply; Glycol Return | Carbon Steel Sch40 or SS304L | Victaulic/Press/BW | Glycol
PIQ REF-01 | Refrigeration Suction; Refrigeration Liquid; Refrigeration Hot Gas | Type L Copper or ASTM A312 SS | Brazed/Welded | Refrigeration
PIQ VAC-01 | Vacuum; Process Vacuum; Vacuum Air | Carbon Steel or SS304L | Threaded/Welded | Vacuum
PIQ VEX-01 | Vacuum Pump Exhaust | Carbon Steel | Threaded/Welded | Exhaust
PIQ GAS-01 | Nitrogen; Carbon Dioxide; Argon; Helium | ASTM A312 304L SS | Compression/Weld | Inert gases
PIQ OXY-01 | Oxygen | Cleaned 316L SS | Orbital/BW | Oxygen service
PIQ HYD-01 | Hydrogen | 316L SS | Orbital/BW | Hydrogen
PIQ LPG-01 | Propane; LPG; LNG | ASTM A106 Gr.B | BW | Fuel gas
PIQ AMM-01 | Ammonia | ASTM A106 Gr.B | BW | Ammonia
PIQ IG-01 | Instrument Gas | 316L SS tubing | Compression | Analyzer gas
PIQ BA-01 | Breathing Air | 316L SS or Aluminum | Compression | Breathing air
PIQ SA-01 | Service Air | Aluminum | Push-connect | Utility air
PIQ DCW-01 | Domestic Cold Water | Copper Type L | Solder/Press | Plumbing
PIQ DHW-01 | Domestic Hot Water; Domestic Hot Water Return | Copper Type L | Solder/Press | Plumbing
PIQ RO-01 | RO Feed Water; RO Water; RO Reject | PVC/CPVC/SS | Solvent/Weld | RO
PIQ SW-01 | Soft Water | CPVC | Solvent | Water
PIQ PWP-01 | Process Water | CPVC or CS | Solvent/Victaulic | Process
PIQ BFW-01 | Boiler Feed Water | Carbon Steel A106 | BW | Boiler
PIQ BBD-01 | Boiler Blowdown | Carbon Steel A106 Sch80 | BW | Boiler
PIQ COND-01 | Condensate Return; Condensate Drain | Carbon Steel A53 | Threaded/BW | Condensate
PIQ DM-01 | Demineralized Water | 316L SS | Orbital | High purity
PIQ UPW-01 | Ultra Pure Water | PVDF or 316L EP | Fusion/Orbital | Semiconductor
PIQ PWFI-01 | Purified Water; Water for Injection | 316L EP | Orbital | Pharma
PIQ CIP-01 | CIP Supply; CIP Return; COP | 316L Sanitary Tube | Tri-clamp/BW | Food
PIQ CSTM-01 | Clean Steam; Culinary Steam | 316L SS | BW | Sanitary steam
PIQ PSTM-01 | Process Steam | Carbon Steel A106 | BW | Steam
PIQ SCOND-01 | Steam Condensate | Carbon Steel A53 | Threaded/BW | Steam
PIQ FSTM-01 | Flash Steam | Carbon Steel A106 | BW | Steam
PIQ SVNT-01 | Steam Vent | Carbon Steel | BW | Steam
PIQ PDR-01 | Process Drain; Clean Drain | PVC/CPVC | Solvent | Drain
PIQ OW-01 | Oily Waste | Carbon Steel | Threaded | Waste
PIQ CHD-01 | Acid Waste; Caustic Waste; Neutralization Waste; Chemical Drain | CPVC/PVDF | Solvent/Fusion | Chemical waste
PIQ SD-01 | Storm Drain; Roof Drain; Equipment Overflow; Floor Drain Header | Cast Iron or PVC DWV | No-hub/Solvent | Drainage