MASTER SPECIFICATION

11/13

SECTION 15100 [23 05 29]

PIPE HANGERS AND SUPPORTS

# - GENERAL

## RELATED DOCUMENTS:

### The requirements of the General Conditions, Special Conditions and Section 15010 [23 00 00], Mechanical General, apply to all work specified in this section.

## GENERAL REQUIREMENTS:

### Furnish hangers to support the required loads. Where necessary, design supports to permit movement due to expansion and contraction. Where the drawings show details of supports and anchors, conform to details shown. Where details are not shown, conform to general requirements specified herein.

### Do not use "C" clamps to support pipe hangers from the structure.

### Do not pierce waterproofing or insulation vapor barrier with supports or support bolts.

### All ferrous metal hangers, supports and rods shall be cadmium plated or galvanized.

## QUALITY ASSURANCE:

### All hangers, support, anchors and guides shall be in accordance with the American National Standard Code for Pressure Piping, ANSI/B31.1 with Addenda 31.1 OA-69 and Federal Specification WW-H-17.

### Provide an adequate piping suspension system using standard commercially available pipe hangers and accessories.

### Hang horizontal suspended pipes using adjustable pipe hangers with bolted hinged loops or turnbuckles. Do not use chains, wire, perforated strap iron, flat steel straps or similar construction.

### Submit fastening methods to the Architect for approval by the structural engineer.]

# - PRODUCTS

## CHILLED [AND CONDENSER] WATER SERVICE:

### Suspended insulated pipe [8" and smaller and un-insulated pipe 12" and smaller]:

#### Upper attachments:

##### Support piping in [new] concrete construction with adjustable type inserts.

Grinnell Figure 282

B-Line Figures B3014 and B3014N

Elcen Figure 65

##### Support piping in [existing] concrete construction with cadmium plated, malleable iron expansion case anchor.

Grinnell Figure 117

B-Line Series LA

Elcen Figure 212

##### Where hangers are required between structural concrete beams provide side beam brackets attached to the upper 1/3 of the beam, and all auxiliary steel for the installation of the pipe hangers. Supports shall be designed in accordance with the AISC Steel Handbook.

Grinnell Figure 202

B-Line Figure B3062

Elcen Figure 27

##### Support piping in steel construction with adjustable beam clamps and tie rods.

Grinnell Figure 218

B-Line Figure B3054

Elcen Figure 95 and 76

##### Where hangers are required between structural steel beams or joists provide a welded steel bracket sized to meet the constraints of the structural installation. The bracket shall be attached with a continuous weld between the support and the structural member. Supports shall be designed in accordance with the AISC Steel Handbook.

Grinnell Figure 195

B-Line Figure B3066

Elcen Figure 57

#### Intermediate attachments:

##### Supports for horizontal piping shall be all threaded carbon steel, ASTM A-107 of the following sizes:

Pipe Size     		Hanger Rod

Diameter

2" and smaller		3/8"

2-1/2"			1/2"

3"				1/2"

4"				5/8"

6"				7/8"

8"				7/8"

10"				7/8"

12"				7/8"

#### Pipe attachments:

##### Hangers for horizontal piping shall be clevis type with vertical adjustment. Hangers for insulated pipes shall be selected to bear on a pipe shield outside of the insulation.

Grinnell Figure 260

B-Line Figure B3100

Elcen Figure 12

##### Hangers for multiple horizontal piping shall be trapeze type.

Grinnell Figure 46

B-Line Figure B22

Unistrut Model P3200

Michigan Hanger Figure 380

##### Provide an insulation protection shield between the hangers and the pipe insulation.

Grinnell Figure 167

B-Line Figure B3151

Elcen Figure 400

### Suspended insulated pipe 10" and larger and un-insulated pipe 14" and larger:

#### Upper attachments:

##### Upper attachments shall support piping in [new] concrete construction with a continuous type insert or a rod attachment concrete plate with four 7/8" wedge anchors.

Continuous Insert	 	Rod Plate

Unistrut Model P3200 		Grinnell Figure

52/1175

B-Line Figure B22	 	B-Line Figure

3085/WA

Michigan Hanger	   		Michigan Hanger

Model 380	    			Model 374A/345-5

##### Where hangers are required between structural concrete beams provide side beam brackets attached to the upper 1/3 of the beam and all auxiliary steel for the installation of the pipe hangers. Supports shall be designed and installed in accordance with the AISC Steel Handbook.

Grinnell Figure 202

B-Line Figure B3062

Elcen Figure 27

##### Where hangers are required between structural steel beams or joists provide a welded steel bracket sized to meet the constraints of the structural installation. The bracket shall be attached with a continuous weld between the support and the structural member. Supports shall be designed in accordance with the AISC Steel Handbook.

Grinnell Figure 195

B-Line Figure B3066

Elcen Figure 57

#### Intermediate attachments:

##### Support for insulated horizontal piping shall be all threaded carbon steel, ASTM A-107 of the following sizes:

Pipe Size		Hanger Rod

Diameter

10"			7/8"

12"			7/8"

14"			1"

16"			1"

18"			1"

20" 			1-1/4"

##### Supports for un-insulated horizontal piping shall be all threaded carbon steel, ASTM A-107 of the following sizes:

Pipe Size		Hanger Rod

Diameter

14"			1"

16"			1"

18"			1"

20" 		 	1-1/4"

#### Pipe attachments:

##### Hangers for horizontal piping shall be clevis type with vertical adjustment or trapeze type as required.

Clevis Type			Trapeze Type

Grinnell Figure 260 		Grinnell Figure 46

B-Line Figure B3100		B-Line Figure B11

Elcen Figure 12	 		Unistrut Model P1000 Michigan Hanger 435

##### Where trapeze type hangers are used provide a standard U-bolt attachment for securing the pipe to the hanger.

Grinnell Figure 137

B-Line Figure

Elcen Figure 68A

##### Provide an insulation protection shield between the hanger and the pipe insulation.

Grinnell Figure 167

B-Line Figure B3151

Elcen Figure 400

### Wall supports:

#### Where piping is run adjacent to walls or steel columns welded steel brackets may be used. The bracket shall either be bolted to the wall with a back plate or welded to a mounting flange then attached to the wall or column. The back plate or flange shall be of such size and thickness as to distribute the weight properly.

Grinnell Figure 195

B-Line Figure B3066

Elcen Figure 57

#### Insulated pipes shall be provided with a protection shield between the hanger and the pipe insulation.

Grinnell Figure 167

B-Line Figure B3151

Elcen Figure 400

### Floor supports:

#### Where pipe runs are located next to the floor the pipe shall be supported with an adjustable pipe saddle support and floor flange.

Grinnell Figure 264

B-Line Figure B3092

Elcen Figure 50

#### Vertical piping shall be supported at every floor using riser clamps. Provide a steel plate and neoprene sandwich type pad at each riser clamp for support.

Grinnell Figure 261

B-Line Figure B3373

Elcen Figure 1

## HOT WATER SERVICE:

### Suspended insulated pipe [8" and smaller]:

#### Upper attachments:

##### Support piping in [new] concrete construction with adjustable type inserts.

Grinnell Figure 282

B-Line Figures B3014 and B3014N

Elcen Figure 65

##### Support piping in [existing] concrete construction with cadmium plated, malleable iron expansion case anchor.

Grinnell Figure 117

B-Line Series LA

Elcen Figure 212

##### Where hangers are required between structural concrete beams provide side beam brackets attached to the upper 1/3 of the beam and all auxiliary steel for the installation of the pipe hangers. Supports shall be designed and installed in accordance with the AISC Steel Handbook.

Grinnell Figure 202

B-Line Figure B3062

Elcen Figure 27

##### Support piping in steel construction with adjustable beam clamps and tie rods.

Grinnell Figure 218

B-Line Figure B3054

Elcen Figures 95 and 76

##### Where hangers are required between steel structural beams or joists provide a welded steel bracket sized to meet the constraints of the structural installation. The bracket shall be attached with a continuous weld between the support and the structural member. Supports shall be designed in accordance with the AISC Steel Handbook.

Grinnell Figure 195

B-Line Figure B3066

Elcen Figure 57

#### Intermediate attachments:

##### Supports for horizontal piping shall be all threaded carbon steel, ASTM A-107 of the following sizes:

Pipe Size			Hanger Rod

Diameter

2" and smaller		3/8"

2-1/2"			1/2"

3"				1/2"

4"				5/8"

6"				7/8"

8"				7/8"

#### Pipe attachments:

##### Hangers for horizontal piping shall be adjustable steel yoke pipe roll selected to bear on the outside of the insulation.

Grinnell Figure 181

B-Line Figure

Elcen Figure

##### Provide a pipe covering protection saddle between the hanger and the pipe insulation. Saddle shall be selected to match the insulation thickness such that the lip of the saddle rests on the pipe not the insulation.

Grinnell Figures 160, 161 and 162

B-Line Figures B3161, B3162 and B3163

Elcen Figures 252, 253 and 254

### Wall supports:

#### Where piping is run adjacent to walls or steel columns welded steel brackets may be used. The bracket shall be either bolted to the wall with a back plate or welded to a mounting flange then attached to the wall or column. The back plate or flange shall be of such size and thickness as to distribute the weight properly.

Grinnell Figure 195

B-Line Figure B3066

Elcen Figure 57

#### Pipe shall be supported with a pipe roll and plate welded to the wall bracket.

Grinnell Figure 277

B-Line Figure B311951

Elcen Figure 22

#### Provide a pipe covering protection saddle between the roll support and the pipe insulation. Saddle shall be selected to match the insulation thickness such that the lip of the saddle rests on the pipe not the insulation.

Grinnell Figures 160, 161 and 162

B-Line Figures B3160, B3162 and B3163

Elcen Figures 252, 253 and 254

### Floor supports:

#### Where pipe runs are located next to the floor the pipe shall be supported with an adjustable pipe roll stand with base plate.

Grinnell Figure 274

B-Line Figure B3118SL

Elcen Figure 20

#### Vertical piping shall be supported at every floor using riser clamps. Provide a steel plate and neoprene sandwich type pad at each riser clamp for support.

Grinnell Figure 261

B-Line Figure B3373

Elcen Figure 1

#### Provide a pipe covering protection saddle between roll support and the pipe insulation. Saddle shall be selected to match the insulation thickness such that the lip of the saddle rests on the pipe not the insulation.

Grinnell Figures 160, 161 and 162

B-Line Figures B3160, B3162 and B3163

Elcen Figures 252, 253 and 254

### Expansion attachments:

#### To compensate for expansion of the pipe provide a carbon steel pipe alignment guide welded or bolted to the structure.

Grinnell Figure 256

B-Line Figures B3281 thru B3283

Elcen Figure 411

## PLUMBING SERVICE:

### Suspended domestic cold, hot, hot water return, [gas,] [compressed air,] drainage, [vacuum,] [fuel oil,] waste and vent piping:

#### Upper attachments:

##### Support piping in [new] concrete construction with adjustable type inserts.

Grinnell Figure 282

B-Line Figures B3014 and B3014N

Elcen Figure 65

##### Support piping in [existing] concrete construction with cadmium plated, malleable iron expansion case anchor.

Grinnell Figure 117

B-Line Series LA

Elcen Figure 212

##### Where hangers are required between structural concrete beams provide side beam brackets attached to the upper 1/3 of the beam, and all auxiliary steel for the installation of the pipe hangers. Supports shall be designed in accordance with the AISC Steel Handbook.

Grinnell Figure 202

B-Line Figure B3062

Elcen Figure 27

##### Support piping in steel construction with adjustable beam clamps and tie rods.

Grinnell Figure 218

B-Line Figure B3054

Elcen Figure 95 and 76

##### Where hangers are required between structural steel beams or joists provide a welded steel bracket sized to meet the constraints of the structural installation. The bracket shall be attached with a continuous weld between the support and the structural member. Supports shall be designed in accordance with the AISC Steel Handbook.

Grinnell Figure 195

B-Line Figure B3066

Elcen Figure 57

#### Intermediate attachments:

##### Supports for horizontal piping shall be all threaded carbon steel, ASTM A-107 of the following sizes:

Pipe Size			Hanger Rod

Diameter

2" and smaller		3/8"

2-1/2"			1/2"

3"				1/2"

4"				5/8"

6"				3/4"

8"				7/8"

#### Pipe attachments:

##### Hangers for horizontal piping shall be clevis type with vertical adjustment. Hangers for insulated pipes shall be selected to bear on the outside of the insulation.

Grinnell Figure 260

B-Line Figure B3100

Elcen Figure 12

##### Hangers for multiple horizontal piping systems shall be trapeze type.

Grinnell Figure 46

B-Line Figure B22

Unistrut Model P3200

Michigan Hanger Figure 380

##### Provide an insulation protection shield between all hangers and the pipe insulation.

Grinnell Figure 167

B-Line Figure B3151

Elcen Figure 400

### Wall supports:

#### Where piping is run adjacent to masonry walls or steel columns welded steel brackets may be used. The bracket shall be either bolted to the wall with a back plate or welded to a mounting flange then attached to the wall or column. The back plate or flange shall be of such size thickness as to distribute the weight properly.

Grinnell Figure 195

B-Line Figure B3066

Elcen Figure 57

#### Insulated pipe shall be provided with a protection shield between the hanger and the pipe insulation.

Grinnell Figure 167

B-Line Figure B3151

Elcen Figure 400

### Floor supports:

#### Where pipe runs are located next to the floor the pipe shall be supported with an adjustable pipe saddle support and floor flange.

Grinnell Figure 264

B-Line Figure B3092

Elcen Figure 50

#### Vertical piping shall be supported at every floor using riser clamps. Provide a steel plate and neoprene sandwich type pad at each riser clamp for

#### support.

Grinnell Figure 261

B-Line Figure B3373

Elcen Figure 1

### Chase supports:

#### Support piping in wall spaces behind plumbing fixtures with manufactured brackets and plastic grip clamps systems.

B-Line Ruff-in Series

Sioux Chief Hold Rite

Hubbard

### [Cast Iron No Hub Pipe and Fitting Restraint:

#### Description: CISPI Designation 310-11, CISPI Designation 301-09 , large diameter no-hub cast iron fittings, over 4 inch in size, shall be provided with supplemental support to minimize the risk of joints separation under high thrust conditions. Auxiliary restraint products used shall be manufactured assemblies with thrust pressure rating adequate for the specific installation. Field devised methods and materials shall not be used to accomplish this application solution.

##### Basis-of-Design Product:  Subject to compliance with requirements, provide pipe and fitting restraints of sufficient strength and durability to withstand thrust forces equivalent to 50 feet head pressure.  Restraints shall be designed and manufactured for the specific purpose of restraining hubless cast iron pipe and fittings against separation under thrust forces equivalent to 50 feet head pressure.]

# - EXECUTION

## INSTALLATION:

### Support horizontal equipment such as in-line pumps, [strainers and air separators] independently of the piping system.

### Hang pipe from substantial building structure. Do not hang pipe from other piping, ductwork, ceilings or steel decking.

### Support each horizontal length of no-hub cast iron pipe within 18" of each joint and a maximum of 10'-0" on centers, and as required to maintain alignment and to prevent sagging. Support and anchor pipe in accordance with manufacturers recommendations.

### Horizontal no-hub cast iron pipe 5" and larger shall be suitably braced to prevent horizontal movement in accordance with CISIPI 310. This shall be done at every branch opening or change of direction by use of braces, blocks, rodding or other suitable method, to prevent movement.

### Provide a hanger within one foot of each elbow.

### Support vertical piping at every floor using riser clamps. Secure vertical piping drops along columns or walls at the top and bottom of the drop and every 10'-0" on center.

### Provide a hanger within one foot of each riser in addition to the riser clamp support at every floor.

### Support all fire protection piping independently of all other piping. Refer to Section 15350 [21 00 00], Automatic Sprinkler System.

### Isolate copper tubing from steel supports, anchors and metal studs to prevent electrolysis. Isolate piping with neoprene pads, sheet lead strips or plastic inserts. Duct tape shall not be used to isolate piping.

### Spacing of hangers and supports for above-ground horizontal piping shall be as follows:

Maximum Spacing of

Nominal Pipe Size	Supports

#### Steel pipe

1-1/4" and smaller	7'-0"

1-1/2"			9'-0"

2"				10'-0"

2-1/2"			11'-0"

3"				12'-0"

4"				14'-0"

5"				16'-0"

6"				17'-0"

8"				19'-0"

10"				20'-0"

12"				23'-0"

#### Copper tubing

1/2"				5'-0"

3/4"				5'-0"

1"				6'-0"

1-1/4"			7'-0"

1-1/2"			8'-0"

2"				8'-0"

2-1/2"			9'-0"

3"				10'-0"

4"				12'-0"

5"				13'-0"

6"				14'-0"

#### PVC pipe

2" and smaller		5'-0"

2" thru 6"			8'-0"

8" and larger		10'-0"

#### Cast iron pipe

2" and larger		10'-0"

END OF SECTION