MASTER SPECIFICATION

06/06

SECTION 15510 [23 52 23]

CAST IRON HYDRONIC HEATING BOILER, POWER BURNER,

GAS, OIL, OR COMBINATION GAS/OIL

# - GENERAL

## RELATED DOCUMENTS:

### The requirements of the General Conditions, Special Conditions and Section 15010 [23 00 00], Mechanical General, apply to all work specified in this section.

## QUALITY ASSURANCE:

### Codes and regulations referred to are minimum standards. Where the requirements of the specifications or drawings exceed those of the codes and regulations the drawings and specifications shall govern.

### Boiler and burner shall be the manufacturer's standard commercial product. Boiler manufactured by, Thermo-Pack, Rite, or Ajax will be acceptable.

## OPERATING CONDITIONS:

### The fuel to be used for the boiler shall be natural gas and liquefied petroleum [LP] gas [No. 2 fuel oil and natural gas].

### Natural gas shall have a heat value of 1000 BTU per cubic foot and a specific gravity of 0.6.

### L.P. gas shall have a heat value of 2600 BTU per cubic foot and a specific gravity of 1.5 - 2.0.

### No. 2. fuel oil shall have a heat value of 141,000 BTU per gallon of fuel and a specific gravity of 25-45.

# - PRODUCTS

## BOILER:

### Provide a packaged cast iron boiler-burner unit for use with natural [LP] gas, [light oil] [combination gas/oil] with an output capacity as shown on the drawings complete with firing equipment, combustion chamber, insulation with steel jacket, safety and operating controls, integral electrical wiring and other appurtenances to make the boiler a complete, self contained, fully-automatic unit, ready for service upon completion of utility connections. The entire boiler-burner unit shall be UL labeled.

### Boiler shall be AGA certified for a minimum efficiency of 80%. The boiler shall be constructed, tested and installed in accordance with the ASME Boiler and Pressure Vessel Code Section IV and stamped for 60 psig maximum water working pressure and a maximum temperature of 250 degrees F.

### Sections shall be fine grained cast iron with perimeter joints permanently pressure sealed with high temperature ceramic fiber rope. Cleanout covers, slide dampers and burner mounting plate shall be cast iron. Provide cast iron cleanout covers and frames in front and rear of boiler to allow full access to the heating surface for cleaning.

### Boiler jacket shall be 20 gauge steel with baked enamel finish. Jacket shall be removable for cleaning. The entire jacket shall be insulated with fiberglass insulation.

### Burner shall be pressure-atomizing forced draft type designed for natural [LP] gas [No. 2 fuel oil and natural gas]. Oil pump shall be integral with the burner.

## COMBUSTION EQUIPMENT:

### Equipment shall include forced draft fan with air damper, dual controls (limit and operating), flame sensing device, NEMA-1A control cabinet containing electronic flame safeguard and programmer, control circuit switch, necessary switching relays, numbered wiring and engraved nameplates.

### Controls shall be 115 volt, 60 hertz, single phase. Necessary fuses, motor contactor or magnetic motor starters with thermal overload protection and a step-down control circuit transformer shall be provided with the control cabinet. Four indicating lights shall be provided: low water, flame failure, ignition and main flame.

### The pilot assembly and flame scanner shall be located on the outside of the burner to allow easy adjustment and maintenance. Spring loaded roller cam followers shall be provided for positive positioning of the air damper and fuel valves throughout the operating range. The unit shall have modulating firing sequence with low fire start.

## GAS BURNER:

### Gas burner shall be of the annular port, flame retention, multiple orifice, forced draft type with gas-electric ignition, full modulation with low-fire start and high fire potentiometer.

### The gas train shall be UL approved and IRI type and shall consist of the following minimum components.

#### Lubricated plug cocks.

#### Pilot gas pressure regulator.

#### Pilot gas valve.

#### Gas pressure regulator.

#### Low and high gas pressure cut-off.

#### Motorized safety shut-off valve.

#### Motorized modulating operating gas valve.

#### Normally open vent valve.

#### Provision for pressure test upstream and downstream of the safety and operating gas valves.

#### Low fire start thermostat to limit firing until the unit temperature reaches 180 degrees F.

#### The pilot shall be lighted only when the boiler is calling for heat.

## OIL BURNER:

### The oil burner shall be the pressure atomizing, forced draft type with gas-electric ignition, full modulation with low fire start and high fire potentiometer, with oil pump mounted on the package.

### The oil nozzle gun assembly shall be easily removable without disconnecting any internal piping or fasteners.

### The oil burner shall be UL and IRI approved and shall consist of the following minimum components:

#### Atomizing oil nozzles.

#### Dual oil solenoid valves.

#### Oil filters.

#### Oil metering control valve with adjustable cam operator.

#### Direct spark ignition transformer.

#### Oil pressure regulator and pressure gauges.

#### Air flow safety switch.

#### Oil pump.

## COMBINATION GAS/OIL BURNER:

### Provide a manual switch on the control cabinet to select gas or oil.

### Gas burner shall be of the annular port, flame retention, multiple orifice, forced draft type with gas-electric ignition, full modulation with low-fire start and high fire potentiometer.

### The gas train shall be UL approved and IRI type and shall consist of the following minimum components.

#### Lubricated plug cocks.

#### Pilot gas pressure regulator.

#### Pilot gas valve.

#### Gas pressure regulator.

#### Low and high gas pressure cut-off.

#### Motorized safety shut-off valve.

#### Motorized modulating operating gas valve.

#### Normally open vent valve.

#### Provision for pressure test upstream and downstream of the safety and operating gas valves.

#### Low fire start thermostat to limit firing until the unit temperature reaches 180 degrees F.

#### The pilot shall be lighted only when the boiler is calling for heat.

### The oil burner shall be the pressure atomizing, forced draft type with gas-electric ignition, full modulation with low fire start and high fire potentiometer, with oil pump mounted on the package.

### The oil nozzle gun assembly shall be easily removable without disconnecting any internal piping or fasteners.

### The oil burner shall be UL and IRI approved and shall consist of the following minimum components:

#### Atomizing oil nozzles.

#### Dual oil solenoid valves.

#### Oil filters.

#### Oil metering control valve with adjustable cam operator.

#### Direct spark ignition transformer.

#### Oil pressure regulator and pressure gauges.

#### Air flow safety switch.

#### Oil pump.

## BOILER TRIM:

### Boiler trim shall include, but not be limited to, the following:

#### ASME rated side discharge relief valve sized for 1.25 times the rated output of the boiler and set at [60 psig].

#### Combination pressure/temperature gauge.

#### Built-in air eliminating fitting.

#### Float type low water cut-off with manual reset feature.

#### Pre-wired control panel.

#### Main cock, burner cock, pilot cock and miscellaneous cock shall be designed for gas service with operating handle attached and parallel to gas flow in the open position, when installed in the manifold.

#### Drain tapping with the drain valve.

#### Stack thermometer with scale range 150 to 750 degrees F mounted in the flue gas outlet.

#### Combination water feed and low water cut-off.

## CONTROLS:

### Boiler controls shall include, but not be limited to, the following:

#### Operating temperature control.

#### High limit temperature control to limit the maximum boiler water temperature to 240 degrees F.

#### Electronic flame failure safeguard, with 2-4 second response to flame failure and 15 seconds safety timing

#### Ultra-violet flame detector.

#### Ignition transformers.

#### Interrupted pilot gas control with electronic ignition.

#### Safety shut-off valve with proof of closure.

#### Modulating firing, low fire start.

#### Emergency disconnect switch.

#### Boiler control circuits including safety control circuits, shall be single-phase, two wire, one side grounded, and not over 120 volts. All wiring shall be contained in conduit. Overcurrent protection shall be provided.

#### [Lead-lag control system for multiple boiler installations.]

#### Electrically operated 4 inch diameter alarm bell, wired so that switching off the alarm following a safety shutdown will not prevent the alarm from sounding again upon a recurrence of a subsequent shutdown condition.

# - EXECUTION

## GENERAL:

### Emergency disconnect switch shall be located on the wall outside the boiler room entrance or just inside the door to allow rapid and complete shutdown of the boiler in the event of an emergency. Emergency switch shall be a 30 amp fused type safety switch. Switch shall be painted red and shall be provided with a label indicating the function of the switch.

### Main gas shut-off cock shall be installed with the operating handle attached and parallel to the direction of gas flow in the open position.

### Provide city water make-up to the boiler. Include a water make-up assembly which shall include a reduced pressure type of backflow preventer acceptable to the local authorities.

### Connect hot water lines and pump to the boiler with adequate drains to flush and drain the system.

### Provide a dirt pocket wherever a drop is made in the gas piping to the boiler.

### Appliance and pilot regulators shall be vented to the outside separately from the vent valve vent line.

### Gas valve vent line shall conform to the following:

Fuel Line Size			Vent Line Size

Up to 1-1/2"			3/4"

2"					1"

2-1/2"-3"				1-1/4"

3-1/2"				1-1/2"

4 to 5"				2"

5-1/2" to 6"			2-1/2"

6-1/2" to 7 1/2"			3-1/2"

## CLEANING:

### Fill the boiler with water and pressure test the boiler and system up to the rating the relief valve. Clean the system with trisodium phosphate or equal cleaner, flush the system to remove all trash and dirt and refill the system including inhibitor and antifreeze as specified.

### Bleed the gas line in safe manner and energize the boiler.

## FIELD TESTS:

### Provide the services of a factory trained technician to adjust and start-up the boiler and to instruct the operating personnel. A start-up report shall be furnished to the Architect.

### Operate the boiler and all appurtenances prior to final testing and ensure that all necessary adjustments have been made. Provide testing equipment including gauges, thermometers, calorimeter, Orsat apparatus, thermocouple pyrometers, fuel flow meters, water meters and other equipment required to perform the tests. Draft and pressure may be measured by permanent gauges and meters installed under the Contract. Gas flow may be measured by utility company meters. The tests shall include the following performed, when feasible, in the sequence listed:

#### Strength and tightness tests.

#### Standards compliance tests.

#### Combustion tests.

#### Operational tests.

#### Capacity and efficiency test.

#### Tests of auxiliary equipment.

### Test fuel burning and combustion control equipment with the specified fuel. Report shall include fuel gas analysis composition (Co2, N2, Co, NoX, and H2o) total air by Orsat gas analyzer exit flue gas temperature, stack and combustion loss as a percentage of heat input and percent of excess air.

### Test the boiler continuously for a period of at least 8 hours to demonstrate proper operation of the combustion control, flame safeguard control and safety interlocks. Conduct this test after the adjustment of the combustion controls has been completed under the combustion test.

### Perform the capacity and efficiency test after satisfactory completion of all tests previously specified herein and after the boiler has been operating continuously for 2 days with no nuisance shutdowns. Conduct tests using the specified fuel. Test in accordance with the heat loss method of the ASME Power Test Code PTC 4.1 and report on the ASME Test Form for Abbreviated Efficiency Test. The duration of the tests shall be sufficient to record all necessary data but in no case be less than 4 hours.

## SERVICE AVAILABILITY:

### Submit a certified list of qualified permanent service organizations for the boiler and instrumentation which includes their addresses and qualifications. These service organizations shall be reasonably convenient to the equipment installation and able to render satisfactory service to the equipment on a regular and emergency basis during the warranty period of the Contract. They shall be approved by the boiler manufacturer for warranty service work.

## EQUIPMENT INSTALLATION:

### Install equipment in accordance with installation instructions of the manufacturers. Grout equipment mounted on concrete foundations before piping is installed. Install piping in such a manner as not to bear on any of the equipment. Do not bolt flanged joints tight unless they match. Grade, anchor, guide and support all piping without low pockets.

END OF SECTION