MASTER SPECIFICATION

2/11

SECTION 15020 [23 05 53]

IDENTIFICATION OF PIPING SYSTEMS

# GENERAL

## RELATED DOCUMENTS:

### The requirements of the General Conditions, Special Conditions and Section 15010 [23 00 00], Mechanical General, apply to all work specified in this section.

## VALVE TAGS:

A.	Tag and number all valves in the HVAC and plumbing [and fire protection] systems. Prepare system schematic drawings showing all valves with reference to the valve numbers assigned, framed and mounted on the wall in the mechanical room where directed. Include a copy of these schematic drawings in the Operation and Maintenance manual.

# - PRODUCTS

## PIPE MARKINGS:

### Pipe markings shall be manufactured, pre-printed markers in accordance with the following:

#### No taped or self-adhering markers will be acceptable.

#### Markers shall be strapped in place using nylon fasteners.

#### Markers shall be non-corrosive, non-conducting, mildew resistant and impervious to moisture.

#### Direction of flow arrows shall be placed adjacent to color bands. Band, letter sizes and colors shall be as indicated below.

#### Piping identification markings manufactured by W.H. Brady Co., Seton, Grainger or approved equal will be acceptable.

## PIPE BAND AND LETTER SIZE:

### Pipe band and letter sizes shall conform to ASHRAE standards and the following table:

O.D. of Pipe or		Width of		Size of Letters

Pipe Covering		Color Band		and Numbers

1-1/4" and smaller	8"			1/2"

1-1/2" to 2"		8"			3/4"

2-1/2" to 5"		12"			1-1/4"

6" to 10"			24"			2-1/2"

10" and larger		32"			3-1/2"

## IDENTIFICATION:

### Band legend and letter color shall conform to the following table:

Piping Band			Legend	Letters	Band Color

Chilled Water Supply		CHWS		White		Green

Chilled Water Return		CHWR		White		Green

Condenser Water Supply	CWS		White		Green

Condenser Water Return	CWR		White		Green

Domestic Cold Water		CW		White		Green

Domestic Hot Water		HW		Black		Yellow

Domestic Hot Water

Circulation			HWC		Black		Yellow

Standpipe				SP		White		Red

Automatic Sprinkler		AS		White 	Red

Compressed Air			AIR		Black		Blue

Boiler Feed Water		BFW		Black		Yellow

Boiler Blow Down			BBD		Black		Yellow

Boiler Water			BW		White		Green

Demineralized Water		DMW		White		Green

Distilled Water			DW		White		Green

Fuel Oil Supply			FOS		Black		Yellow

Fuel Oil Return			FOR		Black		Yellow

Soft Water				SW		White		Green

Natural Gas			NAT. GAS	Black		Yellow

Gasoline				GASOLINE	Black		Yellow

Halon					HALON		White		Red

Hot Water Supply			HWS		Black		Yellow

Hot Water Return			HWR		Black		Yellow

Low Pressure Steam		LPS		Black		Yellow

Medium Pressure Steam		MPS		Black		Yellow

High Pressure Steam		HPS		Black 	Yellow

Medical Air			MA		Black		Yellow

Nitrogen				N		White		Black

Oxygen				O		White		Green

Liquefied Petroleum Gas	L.P.GAS	Black		Yellow

Vacuum				VAC		Black		White

Refrigerant Liquid		RL		Black		Yellow

Refrigerant Suction		RS		Black		Yellow

Refrigerant Hot Gas		HG		Black 	Yellow

Drain					D		Black		Green

Low Pressure Condensate	LPC		Black		Yellow

Medium Pressure

Condensate				MPC		Black		Yellow

High Pressure

Condensate				HPC		Black		Yellow

## VALVE TAGS:

### Valve tags shall be circular brass tags 1-1/2" in diameter. The tags shall have the valve number (1/2" minimum height) firmly embossed or engraved and filled with a durable black compound and attached to the valve using copper wire and brass "S" hooks. The valve numbers shall include the following letters to denote which system the valve operates for:

H  - HVAC

P  - PLUMBING

FP - FIRE PROTECTION

# - EXECUTION

## GENERAL:

### Locate piping identification at the following areas:

#### At each riser.

#### At each valve.

#### Where pipes pass through walls and floors (one each side).

#### At or near each change in direction or height.

#### Every 40 feet along continuous runs.

#### Within 4 feet of the entrance or exit to a vessel, tank or piece of equipment.

### Indicate flow direction with arrows of matching style and color and placed so that the arrow points away from the legend.

### A copy of the pipe identification legend shall be [framed and shall accompany the valve tag schematic drawing. In addition, a copy shall be] included in the Operation and Maintenance manual.

### In addition to the above, identify fire protection piping and accessories as outlined in Section 15350 [21 00 00], Automatic Sprinkler System, and in NFPA 13.

END OF SECTION