MASTER SPECIFICATION

3/16

SECTION 15180 [23 07 00]

THERMAL INSULATION FOR MECHANICAL SYSTEMS

PART 1 - GENERAL

## RELATED DOCUMENTS:

### The requirements of the General Conditions, Special Conditions and Section 15010 [23 00 00], Mechanical General, apply to all work specified in this section.

## DESCRIPTION:

### All insulation products shall meet NFPA requirements for a Flame Spread Rating not to exceed 25, a Smoke Developed Rating not to exceed 50 and a Fuel Contributed Rating not to exceed 50.

### Do not use staples for securing insulation.

### Insulation and vapor barrier shall be continuous through wall and floor sleeves, ceilings and roofs [except at fire and fire/smoke dampers].

### Supports for insulated piping shall be outside the insulation. [For pipe sizes 2-1/2 inch and larger provide inserts and pipe shields at pipe hangers.] [For pipe sizes 2 inch and smaller provide pipe shields only at pipe hangers.] [Inserts shall be foam glass or calcium silicate insulation and shall be 2" longer than the pipe shields.] [Use pipe shoes welded to the pipe at roll type hangers.]

### Do not store insulation materials in the building until it is enclosed and dry. Do not install wet insulation.

### Do not apply insulation products with self-sealing type lap jackets at ambient temperatures below 40 degrees F.

### Paint ferrous metal piping installed outdoors with one coat of rust inhibiting primer before installing insulation.

### Do not insulate the following items:

#### Chromium plated brass connections to plumbing fixtures.

#### Underground domestic cold water piping.

#### Domestic cold water piping except where installed above ceilings or in exterior walls.]

#### Piping installed in enclosures for unit ventilators, unit heaters and fin-tube radiation.

#### Discharge piping from pressure relief devices.

#### Factory pre-insulated ducts.

#### Pretreated outdoor air supply ductwork indoors.

#### Exposed-to-sight piping at laboratory tables or concealed piping in laboratory equipment piping compartments.

#### Exposed-to-sight piping at kitchen equipment.

#### Condenser water piping indoors.

#### Loop water piping indoors.

## QUALITY ASSURANCE:

### Codes and regulations referred to in these specifications are minimum standards, however if the requirements of these specifications exceed those of the codes and regulations, the specifications shall govern.

### Any methods of application of insulation products or finishes not specifically detailed herein shall be applied in accordance with the insulation manufacturer's published recommendations. Apply insulation by experienced workers regularly employed in this type of work.

### Insulation products manufactured by Owens-Corning, Johns-Manville, CertainTeed, Knauf or Armstrong will be acceptable.

### Adhesives, mastics and coatings manufactured by Foster, Childers, Insul-Coustic or Minnesota Mining and Manufacturing Co. (3M) will be acceptable.

# - PRODUCTS

## PRE-MOLDED GLASS FIBER PIPE INSULATION:

### Pipe insulation shall be 4 pcf density fibrous glass wool accurately molded to conform to the outside diameter of the pipe. Insulation shall be the one piece snap-on or self-sealing lap type with white all-service jacket and vapor barrier. Insulation shall be suitable for use on hot or cold pipes with a temperature range of 35 to 400 degrees F. Thermal conductivity shall not exceed 0.26 at 75 degrees F mean temperature.

## PRE-MOLDED GLASS FIBER INSULATION THICKNESS IN INCHES:

Up to		1-1/4" to	2-1/2" to	4" and

Service			1"		2"		3-1/2"	Over

Heating systems

Hot water			1"		1-1/2"	1-1/2"	2"

High temp. hot water	1-1/2"	2"		2-1/2"	3-1/2"

Low pressure steam	1"		1-1/2"	1-1/2"	2"

Med. pressure steam	1-1/2"	2"		2-1/2"	3"

High pressure steam	1-1/2"	2"		2-1/2"	3-1/2"

Steam condensate		1"		1"		1-1/2"	2"

Boiler feed water	1"		1"		1-1/2"	2"

Cooling systems

Condenser water		1/2"		3/4"		1"		1"

Condensate drains	1/2"		1"		1"		1-1/2"

Plumbing systems

Hot water and hot

water circulating	1/2"		1"		1"		1-1/2"

Cold water 		1/2"		1/2"		1/2"		1/2"

Steam				1-1/2"	2"		2-1/2"	3"

Steam condensate		1"		1"		1-1/2"	2"

Indirect refrig.

waste				1/2"		1"		1"		1-1/2"

## CELLULAR GLASS PIPE INSULATION:

### Pre-molded pipe insulation shall be 7.5 pcf minimum density rigid cellular glass and vapor barrier with a thermal conductivity not to exceed 0.29 at 75 degrees F mean temperature.

## CELLULAR GLASS INSULATION THICKNESS IN INCHES:

Up to		1-1/4" to	2-1/2" to	4" and

Service			1"		2"		3-1/2"	Over

Cooling systems

Chilled water		1"		1-1/2"	2"		2"

Dual temp. water		1"		1-1/2"	2"		2"

## GLASS FIBER WRAP PIPE INSULATION:

### Pipe insulation shall be 1 pcf density fibrous glass wool wrapping with factory applied all-service jacket. Insulation shall be sealed with vapor barrier tape.

### Insulate the following with 1-1/2" thick glass fiber wrap pipe insulation:

#### Horizontal portions of rain leaders including each elbow and the roof drain body.

#### Vertical portions of rain leaders installed in areas of the building defined as plenums.

#### The P-trap body and the first 10 feet of the horizontal portion of sanitary drain piping whenever a floor drain or hub drain is used for condensate drain or any other drains at low temperature when the floor or hub drain is located on an elevated slab.

## GLASS FIBER SEMI-RIGID BOARD INSULATION:

### Insulation shall be 4 pcf density semi-rigid board material having long glass fibers with resin binder. Thermal conductivity shall not exceed 0.23 at 70 degrees F mean temperature.

### Insulate the following with 1-1/2" thick glass fiber semi-rigid board insulation:

#### Domestic hot water storage tanks.

#### Hot water generators.

#### Air separation tanks.

#### Expansion tanks.

### Insulate the following with 2" thick glass fiber semi-rigid board insulation:

#### Heat exchangers.

#### Condensate pump receivers.

#### Storage tank and heater of deaerators.

#### Flash tanks.

#### Boiler feed pumps.

#### Steam-fed water heaters.

#### Field fabricated plenum housings.

## FOAMED PLASTIC [SHEET AND] TUBING:

### Foamed plastic [sheet and] tubing shall have a minimum density of 4.5 pcf. Thermal conductivity shall not exceed 0.28 at 75 degrees F mean temperature.

### Apply and secure insulation and seal all joints with Armaflex 520, Foster 85-75, or Childers CP-82 adhesive so as to maintain a continuous vapor barrier. On piping, do not split the insulation longitudinally except at branch fittings where it cannot be avoided.

### Insulate the following with 1/2" thick foamed plastic tubing insulation:

#### Domestic hot water piping below ground.

#### Condensate drain piping.

### Insulate the following with 3/4" thick foamed plastic tubing insulation:

#### Refrigerant suction piping. Coat piping outside the building with two coats of white, ultra-violet resistant Armaflex vinyl lacquer or Foster 30-64 coating.

### Insulate the following with 1-1/2" thick foamed plastic sheet adhered to a removable 20 gauge aluminum casing:

#### Chilled water pump heads.

#### Condenser water pump heads.

#### Chiller cooler, water boxes and suction pipe (unless factory insulated).

#### Dehumidifier spray pump head.

#### Hot water pump heads.

#### Strainers.

#### Heat exchanger head sections.

#### Access plates.

#### Couplings.

## MINERAL WOOL BOARD INSULATION:

### Insulation shall be semi-rigid mineral wool board having an average thermal conductivity not to exceed 0.24 at 75 degrees F mean temperature.

### Insulate the following with 2" thick mineral wool board insulation:

#### Kitchen hood exhaust ductwork.

## CALCIUM SILICATE BLOCK INSULATION:

### V-grooved calcium silicate insulation shall have a thermal conductivity not to exceed 0.42 at 200 degrees F mean temperature.

### Insulate the following with 2" thick calcium silicate block insulation:

#### Fabricated single wall boiler breaching and flue.

#### Emergency generator exhaust pipe and muffler except do not insulate the generator flexible connection.

#### Emergency generator exhaust manifold if not factory insulated.

## FIBERGLASS WRAP DUCT INSULATION:

### Insulation shall be 1 pcf minimum density having a thermal conductivity of 0.27 at 75 degrees F mean temperature. Insulation shall have a factory applied vapor barrier of foil-faced flame resistant kraft paper.

### Insulate the following with 2" thick fiberglass wrap duct insulation:

#### All supply ductwork [outside mechanical rooms].

#### All return and relief ductwork [outside mechanical rooms] except ductwork run in return air plenums and internally lined return and relief ducts need not be insulated.

#### All outdoor air ductwork [outside mechanical rooms.]

## FIBERGLASS BOARD DUCT INSULATION:

### Insulation shall be 3 pcf semi-rigid board material having a thermal conductivity not to exceed 0.25 at 75 degrees F mean temperature.

### Insulate the following with 2" thick fiberglass board duct insulation:

#### All supply ductwork inside mechanical rooms.

#### All return, relief and outdoor air ductwork inside mechanical rooms whether internally lined or not.

#### All ductwork installed outdoors.

## ACOUSTICAL DUCT LINER:

### Acoustical duct liner shall be a flexible type having long glass fibers with a smooth, firmly bonded fire-resistant surface specifically designed to prevent erosion of the fibers. Thermal conductivity shall not exceed 0.26 at 75 degrees F mean temperature and the noise reduction coefficient shall be not less than 0.60 when based on the Acoustical Materials Test, Mounting No. 6.

### Completely coat all duct surfaces with Foster 85-60 or Childers CP-127 adhesive. Join sections of liner by coating the edges with Foster 30-36 or Childers CP-50AMV1. Impale the liner on self-adhering pins, secured with self-locking washers, spacing the pins not more than 4" from the edges and not more than 16" on centers.

### Duct liner shall meet the National Board of Fire Underwriters' Standards for Internal Duct Application and shall have a minimum density of 3 pcf. Air friction correction factor shall not exceed 1.40 at 2000 fpm and 1.50 at 4000 fpm.

### Provide 1" thick acoustical duct liner on the following ductwork:

#### Return ductwork where indicated on the drawings.

#### Outdoor air ductwork where indicated on the drawings.

#### Transfer ducts where indicated on the drawings.

## ADHESIVES, MASTICS, COATINGS AND VAPOR BARRIERS:

### The treatment of pipe insulation jackets and duct insulation facings to impart flame spread and smoke developed ratings shall be permanent. The use of water-soluble treatments is prohibited.

### Vapor barriers shall be installed on all pipe and duct insulation which shall have a perm rating of not more than 0.05 perms. Adhesives, coatings and mastics shall have a perm rating of not less than 0.25 perms.

### Vapor Barrier Coatings shall have a perm rating of 0.03 perms or less at 45 mils dry as tested by ASTM E 96.  Foster 30-65 or Childers CP-34.

D.	Weather Barrier Mastics shall be water based.  Foster 46-50 or Childers CP-10/11.

E.	Adhesives for fiberglass shall meet ASTM C 916, Type II.  Foster 85-60 or Childers CP-127.  Water based.

F.	Insulation Joint Sealant (cellular glass) shall be used on all chilled water pipe insulation butt and longitudinal joints wherever cellular glass insulation is used.  Foster 95-50 or Childers CP-76

G.	Metal Jacketing Sealant shall be non hardening elastomeric sealant.  Foster 95-44 or Childers CP-76 shall be used.

H.	Elastomeric Insulation Adhesive shall be Foster 85-75, Childers CP-82 or Armaflex 520

I.	Elastomeric Outer Coating shall be white polyacrylate copolymer emulsion.  Foster 30-64 or Armacell WB coating.

### J.	Lagging Adhesive shall be Foster 30-36 or Childers CP-50AMV1.

## TAPE:

### Whenever tape is used for sealing purposes, it shall be of the type and shall be applied as recommended by the covering manufacturer. If there is no such recommendation, the tape used shall be 3M Adhesive EC-1329.

## INSULATING CEMENT:

### Insulating cement shall be Ramco Thermokote. Where insulating cement is applied to pipe fittings in concealed locations it shall be "one-coat" cement.

## GLASS CLOTH JACKET:

### Glass cloth jacket on pipe, duct and equipment insulation shall be open weave, standard weight. Foster Mast a Fab or Childers Chil Glas #10.

# - EXECUTION

## GENERAL:

### Clean all surfaces to be insulated of all loose scale, dirt, rust, oil and other foreign matter and thoroughly dry before applying insulation.

### Perform pressure tests required by other sections before insulation is applied.

### Where existing insulation is damaged due to demolition or construction operations, remove and replace it with new insulation to match the existing work or as specified herein for new insulation.

### Insulate completely all metal surfaces of piping and ductwork other than hangers.

### Insulation surface finishes shall present a tight, smooth appearance and the surface finish shall be extended to protect all raw ends and edges of the insulation.

## INSULATION FOR PIPING:

### Insulate all valves [including valve bonnets on chilled water piping], strainers, flanges and fittings. Use pre-molded material where available.

### Install insulation materials with smooth and even surfaces, with jackets drawn tight and cemented down smoothly at longitudinal seams and end laps. Do not use scrap pieces of insulation where a full length of insulation will fit.

### Install insulation, jackets and coatings continuous through wall and floor openings and through pipe sleeves.

### Insulate valves, strainers, fittings, and flanges with field fabricated, multiple mitered segments of molded pipe insulation of the same thickness and material as the adjoining pipe insulation. Secure segments with 20 gauge galvanized steel wire and apply a smoothing coat of insulating cement. Use white fabric and vapor barrier mastic on all cold fittings, elbows, strainers, valves flanges exposed to view such as in mechanical rooms.

### Except in return air plenums or where exposed to view, hot pipe fittings may be insulated with precut glass fiber applied in accordance with the manufacturer's recommendations and finished with white one-piece PVC shell covers.

### For foam plastic insulation, butt all joints together and seal with joint straps furnished with the insulation. Secure all jacket laps with lap adhesive.

### Insulate all chilled water [and dual temperature] piping appurtenances such as thermometer wells, gauge cocks, valve stems and the like with [foamed plastic sheet and tubing] [preformed and mitered cellular glass pipe insulation, secured in place with 1/2" wide aluminum bands spaced 18" on center]. Seal all joints with flexible joint sealer and finish with white vapor barrier mastic [reinforced with glass cloth].

### On piping exposed outdoors, oversize the insulation to allow for heat tape, and do not apply insulation until the pipe has been painted and the heat tape applied. For hot water piping, finish the insulation with standard weight glass cloth set in a 1/16" thick bed of weather barrier mastic. After drying, apply a 1/16" coat of specified weather barrier mastic. For chilled water piping, finish insulation with two coats of vapor barrier mastic and glass cloth. Protect insulation, including all fittings, with 0.024" thick corrugated aluminum, overlapped at the seams a minimum of 2", arranged to shed water and secured with aluminum bands spaced not more than 16" apart. Seal all jacketing laps with 1/8” bead metal jacketing sealant as specified.

### Prior to the application of insulation, wire brush piping installed underground [that is not part of a pre-engineered underground piping system] and paint with two coats of cold applied, vapor barrier asphalt cutback mastic similar to Foster 60-25/26 or Childers CP-22/24. After installation in the trench and after testing is complete, paint all joints, welds and fittings the same as for the pipe and then apply insulation as specified herein.

## INSULATION FOR DUCTWORK:

### Cover all standing ribs and seams with insulation. Secure insulation to the duct with specified adhesive applied in 4" strips around the duct on 18" centers. Use nylon cord ties at 18" intervals to secure the insulation on round ductwork. On rectangular [or flat oval] ductwork 36" wide or more in either dimension, secure the insulation to the bottom of the duct using self-adhering pins and self-locking washers spaced not more than 18" on center. Overlap factory applied insulation, where applicable, a minimum of 2". Seal the vapor barrier at all butt joints, laps and breaks using 4" wide foil-reinforced tape.

### Provide insulation, jackets and coatings continuous through wall and floor openings [except do not insulate fire and fire/smoke dampers].

### Secure insulation to kitchen exhaust ductwork using copper wire spaced 24" apart or weld pins on not more than 16" centers. Seal butt joints, edges and breaks with mineral fiber insulating cement. Finish with a 1/4" coat of mineral fiber insulating cement troweled smooth. Do not use adhesive on kitchen exhaust ducts.

### Insulate all ductwork exposed outdoors with 2" thick, 3 pcf density glass fiber semi-rigid board insulation, secured with self-adhering pins and self-locking washers spaced not more than 18" on center. Seal butt joints and edges with mastic. Finish with standard weight glass cloth set in 1/16" thick specified weather barrier. After drying, apply a 1/16" thick finish coat of water barrier mastic.

## INSULATION FOR EQUIPMENT:

### Secure insulation to the equipment with insulation hangers with self locking washers, copper wire or galvanized steel bands. Miter the insulation to ensure a tight fit. Seal all joints with mineral wool insulating cement. Finish with standard weight glass cloth set between two coats of 1/16" thick white mastic.

### Insulate the flanged ends of strainers, removable head sections, pumps, access plates and couplings with a 20 gauge removable aluminum casing, lined with 2" thick foamed plastic sheet, adhered to all inside surfaces of the casing. Fabricate the casing in two sections, joined with galvanized steel bolts, nuts and washers and arranged so that the casing may be removed and reinstalled without damaging the insulation.

## MISCELLANEOUS EQUIPMENT:

### Secure insulation on fabricated single wall boiler breaching and flues, and emergency generator exhaust pipes and mufflers with copper wire or galvanized steel bands. Seal all joints with mineral wool insulating cement and finish with standard weight glass cloth set between two 1/16" coats of specified white weather barrier mastic.

### Insulate bypass chemical feeders and associated piping the same as the piping system in which they are installed.

## CLEANING:

### Prior to final acceptance, clean the finished surfaces of all exposed insulation of all stains and blemishes. If necessary to obtain a new appearance, coat any discolored insulation with off-white latex based semi-gloss paint or lagging adhesive.

END OF SECTION