# MASTER SPECIFICATION

10/16

# SECTION [15310] 23 2160

MECHANICAL GROOVED PIPE COUPLINGS AND FITTINGS

# PART 1 - GENERAL

## 1.01	RELATED DOCUMENTS:

### A.	The requirements of the General Conditions, Special Conditions and Section [15010] 23 0000, Mechanical General, apply to all work specified in this section.

1.02	GENERAL:

- Submittals:

  - Products shall be shown on drawings and product submittals and shall be specifically identified with the applicable style or series number.

- References:

  - American Society for Testing Materials (ASTM):

    - ASTM A-53 – Pipe, Steel, Black and Hot-Dipped Zinc Coated, Welded and Seamless.

    - ASTM A-183 – Carbon Steel Track Bolts and Nuts.

    - ASTM A-234 – Standard Specification For Piping Fittings or Wrought Carbon Steel and Alloy Steel.

    - ASTM A-449 – Quenched and Tempered Steel Bolts and Studs.

    - ASTM A-536 – Ductile Iron Castings.

    - ASTM F-1476 - Standard Specification for Performance of Gasketed Mechanical Couplings for Use in Piping Applications.

  - American Society of Mechanical Engineers:

    - ASME B16.9 – Factory Made Wrought Butt Welded Fittings.

    - ASME B31.1 – Chemical Plant and Petroleum Refining Piping.

    - ASME B31.9 – Building Services Piping.

  - American Water Works Association:

    - AWWA C-606 – Grooved and Shouldered Joints.

- Quality Assurance: To assure uniformity and compatibility of piping components in grooved end piping systems, all grooved products utilized shall be supplied by Victaulic.  Grooving tools shall be supplied by the same manufacturer as the grooved components.

PART 2 - PRODUCTS

2.01	MATERIALS:

A.	Pipe/Grooved (Standard/Light-wall): Carbon Steel, A-53B/A-106B. Roll or cut grooved-ends as appropriate to pipe material, wall thickness, pressures, size and method of joining. Pipe ends to be grooved in accordance with the manufacturer’s current listed standards conforming to ANSI/AWWA C-606.

# B.	Mechanical Couplings for Joining Carbon Steel Pipe:

1.	Standard mechanical couplings, 2 inch through 12 inch: Manufactured in two segments of cast ductile iron, conforming to ASTM A-536, Grade 65-45-12. Gaskets shall be pressure-responsive synthetic rubber, grade to suit the intended service, conforming to ASTM D-2000. Mechanical Coupling bolts shall be zinc plated (ASTM B-633) heat treated carbon steel track head conforming to ASTM A-449 and ASTM A-183, minimum tensile strength 110,000 psi.

- Rigid Type: Coupling housings with offsetting, angle-pattern bolt pads shall be used to provide system rigidity and support and hanging in accordance with ANSI B31.1, B31.9, and NFPA 13.

- Flexible Type: Use in locations where vibration attenuation and stress relief are required. Flexible couplings may be used in lieu of flexible connectors at equipment connections. Three couplings, for each connector, shall be placed in close proximity to the vibration source.

2.	Flange Adapters: For use with grooved end pipe and fittings, flat faced, for mating to ANSI Class 125/150 flanges.

3.	Grooved couplings shall meet the requirements of ASTM F-1476.

4.	Gasket: Synthetic rubber conforming to steel pipe outside diameter and coupling housing, manufactured of elastomers as designated in ASTM D-2000.

a.	Reference shall be made to the latest published manufacturer’s selection guide for gaskets for proper gasket selection for the intended service.

5.	Mechanical couplings, 14 inch through 60 inch: Couplings shall consist of two ASTM A-536 ductile iron housing segments, a wide elastomer pressure responsive gasket, and zinc electroplated carbon steel track head bolts and nuts conforming to the physical and chemical requirements of ASTM A-449 and the physical requirements of ASTM A-183.

- Coupling housings designed with the wedge-shaped AGS key profile to engage the mating pipe wedge-shaped AGS grooves. Housings shall include lead-in chamfer to accommodate a wider acceptable range of initial pipe positions. Housings shall be coated with orange enamel or galvanized.

- Gasket: Wide width, pressure-responsive, synthetic rubber, conforming to steel pipe outside diameter and coupling housing, manufactured of elastomers as designated in ASTM D-2000.

- Coupling types:

  - Rigid coupling: Coupling key shall be designed to fill the wedge shaped AGS groove to provide a rigid joint that corresponds with support spacing as defined by ASME B31.1 and B31.9. Systems incorporating rigid couplings shall require the calculated thermal growth/contraction of the piping system to be fully compensated for in the design of the piping system through use of adequate flexible components.

  - Flexible Coupling: Coupling key shall be designed to fit into the wedge shaped groove and allow for linear and angular movement, vibration attenuation, and stress relief.

  - Flange Adapter 14 inch to 24 inch: For use with AGS grooved end pipe and fittings, flat faced, for mating to ANSI Class 125/ 150 flanges.

C.	Victaulic Grooved End Fittings:

1.	Standard fittings shall be cast of ductile iron conforming to ASTM A-536, Grade 65-45-12, forged steel conforming to ASTM A-234, Grade WPB 0.375" wall, or fabricated from Std. Wt. Carbon Steel pipe conforming to ASTM A-53, Type F, E or S, Grade B. Fittings provided with an alkyd enamel finish or hot dip galvanized to ASTM A-153.  Zinc electroplated fittings and couplings conform to ASTM B633.

2.	AGS Fittings shall be supplied with factory AGS grooved ends, for use with couplings and flange adapter. Fittings shall be manufactured of ductile iron conforming to ASTM A-536, forged carbon steel conforming to ASTM A-234, or factory fabricated from carbon steel pipe conforming to ASTM A-53. Fittings shall be manufactured to the dimensional standards ASME B16.9. Orange enamel coated or galvanized.

3.	Hole-Cut Branch Outlets:

- Bolted Branch Outlet: Branch reductions on 2" through 8" header piping. Bolted branch outlets shall be manufactured from ductile iron conforming to ASTM A-536, Grade 65-45-12, with synthetic rubber gasket, and heat treated carbon steel zinc plated bolts and nuts conforming to physical properties of ASTM A-183.

b.	Strapless Outlet: 1/2" or 3/4" NPT outlet on 4" and larger header sizes rated for 300 PSI.

# D.	Victaulic Tooling:

1.	Tools shall be manufactured and supplied by the manufacturer. Use roll sets or cut groovers compatible with the pipe material and wall thickness per the manufacturer’s installation instructions.

2.	Common wedge shaped AGS groove for pipe sizes 14” through 24” requiring one common AGS roll set per tool, for use with manufacturer’s approved grooving tools.

# PART 3 - EXECUTION

# 3.01	GENERAL:

# A.	Installation:

1.	Pipe ends shall be clean and free from indentations, projections and roll marks in the area from pipe end to groove for proper gasket sealing.

2.	The gasket style and elastomeric material (grade) shall be verified as suitable for the intended service as specified.

3.	Install the piping system in accordance with the latest manufacturer’s installation instructions.

4.	AGS products shall not be installed with standard grooved end pipe or components. Installing AGS products in combination with standard grooved end products could result in joint separation and/or leakage.

5.	Use manufacturer’s grooving tools with AGS roll sets to groove the pipe. Follow the manufacturer’s guidelines for tool selection and operation.

- Couplings installation shall be complete when visual metal-to-metal contact is reached.

B.	Training:

- A factory trained representative shall provide on-site training for the Contractor’s field personnel in the use of grooving tools, application of groove, and product installation.

C.	Application:

- A manufacturer’s representative shall periodically visit the job site and review installation. Contractor shall remove and replace any improperly installed products.

- All grooved components shall conform to local code approval and/or as listed by ANSI-B-31.1, B-31.3, B-31.9, ASME, UL/ULC, FM, IAPMO or BOCA.

- Grooved end product manufacturer to be ISO-9001 certified.

END PF SECTION