## Sheet1
Spec | Service | Service_Abbv | Size | Pipe | Schedule | Coupling | Fitting | Joint | Valve | Flange | Bolts | Clamps | SOLDER | Gasket | Insulation | Support Spacing | Test Pressure | Flexible Hose | MAXIMUM PRESSURE (PSI) | MAXIMUM TEMPERATURE (F) | Thread Compound | Strainers | Traps | o'lets | 90 deg elbow | 45 deg elbow | Tee | Coatings | Lining | Unions
PIQ GR-01 | Chilled Water | CHW | < = 2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Press Fit | Press Fit | Johnson Controls VG1000/VG1245 Series: Popular forged brass, stainless steel trim.Max Pressure: Minimum 150 psi or 250 psi | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket | 8 ft | 225 psig |  | 150 psig | 125 deg F
PIQ GR-01 | Chilled Water | CHW | > 2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Victallic | Victaulic | 150# Butterfly valves (Lug or Wafer style) or OS&Y Gate valves. Double Regulating Valves (DRV) or Venturi Valves | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket |  | 225 psig |  | 150 psig | 125 deg F
PIQ CPVC- 03 | Industrial Water | IW | < = 2" | ASTM D2846 CPVC SDR 11 | Sch 80 | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED. CHECK VALVE 1/2 TO 2 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROLTHREADED OR SOLDER BRONZE BODY,STAINLESS STEEL DISC | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1/2" THICK FOR 1" AND SMALLER,1" FOR 1 1/2" AND LARGER,EXTERIOR: PROVIDE ALUMINUM JACKET,INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  | 150 psig | 125 deg F
PIQ CPVC -03 | Industrial Water | IW | > 2" | ASTM F441 CPVC | Sch 80 | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1" FOR 2" AND LARGER, EXTERIOR: PROVIDE ALUMINUM JACKET, INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  | 150 psig | 125 deg F
PIQ CS-04 | Steam 125# | Stm 125# | < = 2" | Carbon Steel , A106 Gr B | Sch 80 | For forged fittings (e.g., couplings, half-couplings, threaded/socket-welded tees, and unions), the governing material specification is ASTM A105. Dimensional standards depend on the connection type: [1, 2].Socket Weld: ASME B16.11. Threaded (NPT) ASME B1.20.1 | SW ,ASTM A-105 | SW | On/Off Gate CL150 Bronze Cast or Stainless Steel or Ball Steam Rated w/ reinforced TFE 9tEFLON) SEATS TO>350 DEG.F. Globe - Throttling Steam Rated. Check Valve-Bronze or Cast Iron Swing Check Valves with metallic seating, or specialized Silent (Spring-Loaded) Check Valves | 150# ,RF | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  |  | 2" Mineral wool w/ Alum.Jacket |  | 187.5 psig |  | 150 psig | 125 deg F
PIQ CS-04 | Steam 125# | Stm 125# | > 2" | Carbon Steel , A106 Gr B | Sch 40 or Std WT >=12" | Use BW | ASTM A234 | BW | On/Off Gate CL150 Bronze Cast or Stainless Steel or Ball Steam Rated w/ reinforced TFE 9tEFLON) SEATS TO>350 DEG.F. Globe - Throttling Steam Rated. Check Valve-Bronze or Cast Iron Swing Check Valves with metallic seating, or specialized Silent (Spring-Loaded) Check Valves | 150# ,RF | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  |  | 2" Mineral wool w/ Alum.Jacket |  | 187.5 psig |  | 150 psig | 125 deg F
PIQ AL-05 | Compress Air | CA | < = 2" | ASTM B241,ALUMINUM-ALLOY , SEAMLESS PIPE | Sch 10 | Fiber Glass-Reinforced Ployamide Body Push-To-Connect Socket | Fiber Glass-Reinforced Polyamide Body Push-To-Connect Socket | Fiber Glass-Reinforced Polyamide Body Push-To-Connect Socket | Ball Valve Fiberglass-Reinforced Polyamide Body Push To Connect Socket | [7 empty] | 150 psig |  | 150 psig | 125 deg F
PIQ AL -05 | Compress Air | CA | > 2" | ASTM B241,ALUMINUM-ALLOY , SEAMLESS PIPE | Sch 10 | Fiber Glass-Reinforced Ployamide Body Push-To-Connect Socket | Fiber Glass-Reinforced Polyamide Body Push-To-Connect Socket | Fiber Glass-Reinforced Polyamide Body Push-To-Connect Socket | Ball Valve Fiberglass-Reinforced Polyamide Body Push To Connect Socket | [7 empty] | 150psig |  | 150 psig | 125 deg F
PIQ TB-06 | DI | DI | < = 2" | Tubing SMLS or Welded ASTM-270 | OD | Tri- Clamps or Buttwelded | Ferrules w/ TC or TC x BE | Ferrules w/ TC or TC x BE | Sanitary ball valve, 150# forged 316L stainless steel body sanitary TC x TC. Poppet type check valve, 316L SS, sanitary clamp ends, PTFE TCxTC poppet and gasket. Internal finish 20 Ra max. PBM Model VC or HC or approved equal |  |  | Tri-Clamp, 2 piece heavy duty, 304 stainless steel material hand tightened wing nut type. Tri-Clover Type 13MHHM or approved |  | Molded one piece “O” Ring Gasket. For fractional fittings FDA approved. Tri-Clover 42 MP-E, or approved equal. |  |  | 187.5 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length | 150 psig | 125 deg F
PIQ TB -06 | DI | DI | > 2" | Tubing SMLS or Welded ASTM-270 | OD | Tri- Clamps or Buttwelded | Ferrules w/ TC or TC x BE | Ferrules w/ TC or TC x BE | Tri-clamp ends. Internal finish to be same as tubing (20Ra Max) meeting BPE surface designation SF1. Body to be standard satin finish on exterior. Valves to have TEF seats and seals, stainless steel ball and stem, lockable handle,PBM Igenix Series 8 valves or approved equal stainless steel nuts and bolts. |  |  | Tri-Clamp 2-piece, 304 S.S. high pressure, high temperature (For use above |  | Molded one piece “O” Ring Gasket, FDA approved. Tri-Clover Type 1, 40 MP-E, or equal |  |  | 187.5 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length | 150 psig | 125 deg F
PIQ CS-01 | COMPRESSED AIR | CA | < = 2" | THREADED: ANSI B36 STEEL.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK | Sch 80 | ANSI B16.39 CLASS 150, ASTM A197 IRON | THREADED: ANSI B16.3 CLASS 150, ASTM A197 IRON | ANSI B1.20.1 TAPER THREADED(3) | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-01 | COMPRESSED AIR | CA | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD, SOCKET WELD, OR FLANGED, THREADED CONNECTIONS NOT PERMITTED | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | l. |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-02 | Natural Gas | NG | < = 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | ANSI B16.11, ASTM A105 CLASS 3000 STEEL | ANSI B1.20.1 TAPER THREADED(4) | BALL ≤2 1000 PSI THREE PIECE, FULL PORT, BLOW-OFF PROOF STEMSOCKET WELD OR THREADED CARBON STEEL. CHECK 1/2 TO 2 1000 PSI CWP LIFT CHECK THREADED ALL BRONZE .EQUIPMENT SERVICE REGULATORS(1) GLOBE OR ANGLE ≤1 125 INLET, 2.2 MAX OUTLET DIRECT OPERATED, SPRING LOADED, INTERNAL RELIEF THREADED CAST IRON BODY, ALUMINUM ORIFICE, NITRILE O-RINGS NITRILE O-RINGS | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-02 | Natural Gas | NG | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL or SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | PLUG >2 200 CWP LUBRICATED FLANGED CAST IRON BODY, TEFLON COATED PLUG. | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-03 | NATURAL GAS HIGH PRESSURE | NG HP | < = 2" | 1/2'-3/4" ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 160 BLACK STEEL;or ASTM A106, SEAMLESS, GRADE B SCHEDULE 160 BLACK STEEL 1'-2" ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | 1/2"-1" SCH 160,1'-2" Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | ANSI B16.11, ASTM A105 CLASS 3000 | ANSI B1.20.1 TAPER THREADED(3,4) | ,ALL BRONZE. <=1" Pressure Regulator 125 INLET, 2.2 MAX OUTLET,DIRECT OPERATED, SPRING LOADED, INTERNAL RELIEF,THREADED,CAST IRON BODY, ALUMINUM ORIFICE, NITRILE O-RINGS | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, CARBON STEEL CENTERING RING FOR FLAT FACE FLANGES: ANSI B16.21, FULL FACE, 1/8-INCH THICK, PTFE WITH BARIUM SULFATE |  |  | 450 psig |  | 150 psig | 125 deg F
PIQ CS-03 | NATURAL GAS HIGH PRESSURE | NG HP | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL;or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | PLUG,200 CWP,LUBRICATED,FLANGED,CAST IRON BODY, TEFLON COATED PLUG | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, CARBON STEEL CENTERING RING FOR FLAT FACE FLANGES: ANSI B16.21, FULL FACE, 1/8-INCH THICK, PTFE WITH BARIUM SULFATE |  |  | 450 psig |  | 150 psig | 125 deg F
PIQ CS-04 | STEAM, LOW PRESSURE | STM LP | < = 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 STEE | Threaded ANSI B16.11, ASTM A105 CLASS 3000 STEE | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-04 | STEAM, LOW PRESSURE | STMLP | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, LOW PRESSURE: SPIRAL WOUND 150 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-05 | STEAM, MEDIUM PRESSURE | STM MP | < = 2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, LOW PRESSURE: SPIRAL WOUND 150 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 450 psig |  | PRESSURE (PSI)(1): 740 655 600 410 | MAXIMUM TEMPERATURE (F): 100 300 500 800
PIQ CS-05 | STEAM, MEDIUM PRESSURE | STM MP | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, MEDIUM PRESSURE: SPIRAL WOUND 300 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 450 psig |  | PRESSURE (PSI)(1): 740 655 600 410 | MAXIMUM TEMPERATURE (F): 100 300 500 800 MAXIMUMPRESSURE (PSI)(1): 740 655 600 410
PIQ CS-06 | STEAM, HIGH PRESSURE | STM HP | < = 2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3) | ANSI B16.11, ASTM A105 CLASS 3000 | ANSI B1.20.1 TAPER THREADED(3) | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, MEDIUM PRESSURE: SPIRAL WOUND 300 LB GASKET .SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800
PIQ CS-06 | STEAM, HIGH PRESSURE | STM HP | > 2" | ASTM A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, HIGH PRESSURE: SPIRAL WOUND 600 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800
PIQ CS-07 | CHEMICAL | CHEMICAL | < = 2" | 1"-4" THERMALOK STYLE: ASTM A5873 CARBON STEEL, SCHEDULE 40 DIMENSIONS, PTFE LINER and 6"-8" THERMALOK STYLE: ASTM A53, GRADE B CARBON STEEL , SCHEDULE 40 DIMENSIONS, PTFE LINER | Sch 40 | NOT AVAILABLE, USE FLANGED CONNECTIONS,AISI 15V24 STEEL (1"-2") OR ASTM A513 STEEL | ANSI B16.5 ASTM A216 GRADE WCB CAST STEEL, OR FABRICATED CARBON STEEL. | FLANGED | Plastic-Lined Plug or Ball Valves,Tight quarter-turn shutoff, Fully encapsulated bodies and internals where the ball or plug component is either solid plastic or heavily coated in a thick layer of PFA or PTFE, ensuring zero fluid-to-metal contact .Lined Check Valves Flanged Features a poppet-type design where every single surface making contact with the line media is covered with a thick protective layer of plastic to eliminate corrosion and fluid trapping | ROTATING FLANGES: ASTM A395 DUCTILE IRON OR ASTM A105 STEEL; ANSI B16.5 CLASS 150, ASTM A105 STEEL | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, HIGH PRESSURE: SPIRAL WOUND 600 LB GASKET. Verify with Engineer. Consider No Gasket LINER THEMALOK MECHANICALLY LOCKED ASTM F1545 PTFE. MINIMUM LINER FLANGE FACE THICKNESS: 0.1" |  |  | 225 psig |  | MAXIMUM PRESSURE (PSI)(1): 285 260 200 170 | MAXIMUM TEMPERATURE (F): -20 to 100 200 400 450
PIQ CS-07 | CHEMICAL | CHEMICAL | > 2" | 1"-4" -6"-8" SWAGED STYLE: ASTM A513 ERW C-1010 ALUMINUM KILLED CARBON STEEL WITH CHEMICAL COMPOSTION MEETING ASTM A587, SCHEDULE 40 DIMENSIONS, PTFE LINED DIAMOND PICKED SPIRAL GROOVED INTERIOR | Sch 40 | (3"-4"), TAPPED OR STANDARD VENTED COUPLER OVER BUTT WELDED LINER ,>4" NOT AVAILABLE, USE FLANGED CONNECTIONS | ANSI B16.5 ASTM A216 GRADE WCB CAST STEEL, OR FABRICATED CARBON STEEL. | Flanged or MECHANICALLY COUPLED WITH BUTT WELDED LINER AVAILABLE THROUGH 4". | Plastic-Lined Plug or Ball Valves,Tight quarter-turn shutoff, Fully encapsulated bodies and internals where the ball or plug component is either solid plastic or heavily coated in a thick layer of PFA or PTFE, ensuring zero fluid-to-metal contact .Lined Check Valves Flanged Features a poppet-type design where every single surface making contact with the line media is covered with a thick protective layer of plastic to eliminate corrosion and fluid trapping | SLIP-ON, WELD NECK AND SOCKET WELD FLANGES: ANSI B16.5 CLASS 150, ASTM A105 STEELANSI B16.5 CLASS 150, ASTM A105 STEEL, CHAMFERED THREADED FLANGE OR ROTATING FLANGE(5) | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | No Gasket -SWAGED MECHANICALLY LOCKED ASTM F1545 PTFE. MINIMUM LINER FLANGE FACE THICKNESS: 0.1" |  |  | 225 psig |  | MAXIMUM PRESSURE (PSI)(1): 285 260 200 170 | MAXIMUM TEMPERATURE (F): -20 to 100 200 400 450
PIQ CU-01-PW | POTABLE WATER | PW | < = 2" | 1/4"-2" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED) NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PW | POTABLE WATER | PW | > 2" | 2"&3" - ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-NP | NON-POTABLE WATER | NPW | < = 2" | 1/4"TO 2" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01 NP | NON-POTABLE WATER | NPW | > 2" | 3" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PA | PLANT AIR | PA | < = 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PA | PLANT AIR | PA | > 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ-CU -01 F0 | FUEL OIL | FO | < = 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED CODE/ASME B31.9 |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ-CU 01 FO | FUEL OIL | FO | > 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED CODE/ASME B31.9 |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
Spec | Service | Service | Size | Pipe | Schedule | Coupling | Fitting | Joint | Valve | Flange | Bolts | Clamps | SOLDER | Gasket | Insulation | Support Spacing | Test Pressure | Flexible Hose |  | MAXIMUM TEMPERATURE (F): MAXIMUM PRESSURE (PSI)(1): | Jacket/Armour
PIQ-CU-02 | AIR | AIR | < = 2" | Size: < = 1/2" ASTM B68 AND B75 SOFT ANNEALED, BIRGHT SEAMLESS |  |  | ASTM B75 SEAMLESS WROUGHT COPPER |  | BALL <3 600 PSI WOG TWO PIECE, FULL PORT, LEVER HANDLE THREADED OR SOLDER. BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY. CHECK VALVE 1/2 TO 2 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROLTHREADED OR SOLDER BRONZE BODY,STAINLESS STEEL DISC. PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. |  |  |  | SERVICE PRESSURE AND TEMPERATURE LIMITED BY ASME B31.9 AS INDICATED IN THE PIPE SCHEDULE |  |  |  | JACKET: ASTM D1047 PVC, FLAME RETARDANT ARMOR: FLEXIBLE, INTERLOCKING GALVANIZED STEEL
PIQ-CU-02 | INSTRUMENT AIR | IA | < = 2" | Size: < = 1/2" ASTM B68 AND B75 SOFT ANNEALED, BIRGHT SEAMLESS |  |  | ASTM B75 SEAMLESS WROUGHT COPPER |  | BALL <3 600 PSI WOG TWO PIECE, FULL PORT, LEVER HANDLE THREADED OR SOLDER. BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY. CHECK VALVE 1/2 TO 2 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROLTHREADED OR SOLDER BRONZE BODY,STAINLESS STEEL DISC. PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. |  |  |  | SERVICE PRESSURE AND TEMPERATURE LIMITED BY ASME B31.9 AS INDICATED IN THE PIPE SCHEDULE |  |  |  | JACKET: ASTM D1047 PVC, FLAME RETARDANT ARMOR: FLEXIBLE, INTERLOCKING GALVANIZED STEEL
PIQ CS-01 | HOT WATER | HW | < = 2" | THREADED: ANSI B36 STEEL.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK | Sch 80 | ANSI B16.39 CLASS 150, ASTM A197 IRON | THREADED: ANSI B16.3 CLASS 150, ASTM A197 IRON | ANSI B1.20.1 TAPER THREADED(3) | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CS-01 | HOT WATER | HW | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD, SOCKET WELD, OR FLANGED, THREADED CONNECTIONS NOT PERMITTED | Ball Valve 150# Flange RF CS API 608 / ISO 17292ASME B16.10,Check Valve,Swing 150# Flanged RF CS,API 594 / BS 1868ASME B16.10 | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | l. |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CS-01-FO | FUEL OIL | FO | < = 2" | THREADED: ANSI B36 STEEL.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK | Sch 80 | ANSI B16.39 CLASS 150, ASTM A197 IRON | THREADED: ANSI B16.3 CLASS 150, ASTM A197 IRON | ANSI B1.20.1 TAPER THREADED(3) | BALL 500 PSI WOG LEVEL OPERATED, DOUBLE SEAL, UL LISTED THREADED 316 SS BODY AND BALL, TEFLON SEATS. CHECK VALVE 250 PSI WOG Y-PATTERN SWING CHECK THREADED ALL IRON. PRESSURE RELIEF VALVE 150 PSI ADJUSTABLE, SPRING LOADED THREADED BRONZE BODY | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CS-01-FO | FUEL OIL | FO | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD, SOCKET WELD, OR FLANGED, THREADED CONNECTIONS NOT PERMITTED | Ball Valve 150# Flange RF CS API 608 / ISO 17292ASME B16.10,Check Valve,Swing 150# Flanged RF CS,API 594 / BS 1868ASME B16.10 | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | l. |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CPVC- 03 | Plant Water | PW | < = 2" | ASTM D2846 CPVC SDR 11 | Sch 80 | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1/2" THICK FOR 1" AND SMALLER,1" FOR 1 1/2" AND LARGER,EXTERIOR: PROVIDE ALUMINUM JACKET,INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  |  | 150 psig | 125 deg F
PIQ CPVC -03 | Plant Water | PW | > 2" | ASTM F441 CPVC | Sch 80 | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1" FOR 2" AND LARGER, EXTERIOR: PROVIDE ALUMINUM JACKET, INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  |  | 150 psig | 125 deg F
PIQ CA-01 | COMPRESSED AIR | CA | < = 2" | THREADED: ANSI B36 STEEL.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK | Sch 80 | ANSI B16.39 CLASS 150, ASTM A197 IRON | THREADED: ANSI B16.3 CLASS 150, ASTM A197 IRON | ANSI B1.20.1 TAPER THREADED(3) | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ CA-01 | COMPRESSED AIR | CA | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD, SOCKET WELD, OR FLANGED, THREADED CONNECTIONS NOT PERMITTED | Ball Valve 150# Flange RF CS API 608 / ISO 17292ASME B16.10,Check Valve,Swing 150# Flanged RF CS,API 594 / BS 1868ASME B16.10 | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | l. |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  |  | 150 psig | 125 deg F
PIQ-SS-01 | Chemical | CHEMICAL | < = 2" | ANSI B36.19, ASTM A312 or A778, SCHEDULE 40 TYPE 304L STAINLESS STEEL | Sch 40 | ANSI B1.20.1 TAPER THREADED(3)<=100 DEG F BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITT>=200 DEG F | ANSI B16.11, CLASS 3000 ASTM A182 GRADE F304L STAINLESS STEEL <=100 DEG F | ANSI B1.20.1 TAPER THREADED(3)<=100 DEG F BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITT>=200 DEG F | Cast Stainless Valves: Governed by ASTM A351 / ASME SA351 | ANSI B16.5 CLASS 150, ASTM A182 GRADE F304L STAINLESS STEEL, RAISED FACE, SOCKET WELD @ -20 TO 200 DEG F | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK . @ -20 TO 200 DEG F. GASKET MATERIALS SHALL BE SELECTED BASED SERVICE: |  |  | 225 psig |  | 1/2"-2" Pipe 275 PSIG @ 200 DEG F, 2" to 12" Pipe 185 PSIG @ 250 DEG F, 175 PSIG @ 300 DEG F | 1/2" TO 2" Pipe 200 DEG F, 2" TO 12" Pipe 300 DEG F | PROVIDE TEFLON PASTE THREAD LUBRICANT AND SEAL OR TEFLON TAPE FOR THREADED JOINTS. |  |  | USE FITTINGS | [5 empty] | NSI B16.11, CLASS 3000 ASTM A182 GRADE F304L STAINLESS STEEL, SOCKET WELD OR THREADED
PIQ-SS-01 | Chemical | CHEMICAL | > 2" | ANSI B36.19, ASTM A312 or A778, SCHEDULE 40 TYPE 304L STAINLESS STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITT>=200 TO 300 DEG F | BUTT WELD: ANSI B16.9, ASTM A403 CLASS WP304L STAINLESS STEEL. SOCKET WELD: ANSI B16.11, CLASS 3000 ASTM A182 GRADE F304L STAINLESS STEEL .>=200 TO 300 DEG F | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITT>=200 TO 300 DEG F | Forged Stainless Valves: Governed by ASTM A182 / ASME SA182 | ANSI B16.5 CLASS 150, ASTM A182 GRADE F304L STAINLESS STEEL, RAISED FACE, SLIP ON OR WELD NECK. 250 TO 300 DEG F | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS |  |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK . 250 TO 300 DEG F. GASKET MATERIALS SHALL BE SELECTED BASED SERVICE: |  |  | 225 psig |  | 1/2"-2" Pipe 275 PSIG @ 200 DEG F, 2" to 12" Pipe 185 PSIG @ 250 DEG F, 175 PSIG @ 300 DEG F | 1/2" TO 2" Pipe 200 DEG F, 2" TO 12" Pipe 300 DEG F |  |  |  | FOR BRANCHES SAME SIZE OR ONE SIZE SMALLER THAN HEADER: USE FITTING FOR BRANCHES 2 OR MORE SIZES SMALLER THAN HEADER: ASTM A182, CLASS 3000, GRADE F304L STAINLESS STEEL THREADOLET OR WELDOLET | [5 empty] | NOT PERMITTED, UTILIZE FLANGED CONNECTIONS
PIQ-FB-01 | Food & Beverage | F&B | < = 2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5 S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball or True Bore-Self Clean ,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
PIQ-FB-01 | Food & Beverage | F&B | > 2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball True Bore-Self Clean,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
PIQ-SW-01 | Sanitary Waste (Above Grrade) | SW | < = 2" | 1 1/2" (Only not <1 1/2")- Cast Iron (Hubless / No-Hub, CISPI 301, ASTM A888 or PVC Schedule 40 Solid Wall (ASTM D2665, ASTM D1785-Disadvantage: Rarely used above ground in commercial builds because large-diameter Note: PVC expands/contracts heavily with temperature changes and requires massive structural expansion joints. Many commercial plumbing engineers write their specs to allow PVC Schedule 40 for smaller branch lines (≤ 2") to save on labor and material costs, but strictly mandate Cast Iron for all lines larger than 2" (> 2") to control noise from toilets and handle heavy drainage volumes |  | Heavy-duty, 300-series stainless steel shield with multi-band clamps (e.g., Clamp-All 125 or Husky SD) or PVC Schedule 40 PVC DWV (drain, waste, and vent | Heavy-duty cast iron or ductile iron (ASTM A74, ASME B16.12) or PVC Schedule 40 PVC DWV (drain, waste, and vent | Heavy-duty cast iron or ductile iron (ASTM A74, ASME B16.12)
PIQ-SW-01 | Sanitary Waste (Above Grrade) | SW | < = 2" | >=1 1/2" Cast Iron (Hubless / No-Hub, CISPI 301, ASTM A888 or PVC Schedule 40 Solid Wall (ASTM D2665, ASTM D1785-Disadvantage: Rarely used above ground in commercial builds because large-diameter Many commercial plumbing engineers write their specs to allow PVC Schedule 40 for smaller branch lines (≤ 2") to save on labor and material costs, but strictly mandate Cast Iron for all lines larger than 2" (> 2") to control noise from toilets and handle heavy drainage volumes. |  | Heavy-duty, 300-series stainless steel shield with multi-band clamps (e.g., Clamp-All 125 or Husky SD) | Heavy-duty cast iron or ductile iron (ASTM A74, ASME B16.12) | Heavy-duty cast iron or ductile iron (ASTM A74, ASME B16.12)
Glycol
Nitrogen
Spec | Service | Service | Size | Pipe | Schedule | Coupling | Fitting | Joint | Valve | Flange | Bolts | Clamps |  | Gasket | Insulation | Support Spacing | Test Pressure | Flexible Hose |  | MAXIMUM TEMPERATURE (F): MAXIMUM PRESSURE (PSI)(1):
Carbon Dioxide
Oxygen
Argon
Helium
Hydrogen
Propane

## Master_Spec_Template_Full
Spec | Service | Service_Abbv | Size | Pipe | Schedule | Coupling | Fitting | Joint | Valve | Flange | Bolts | Clamps | SOLDER | Gasket | Insulation | Support Spacing | Test Pressure | Flexible Hose | MAXIMUM PRESSURE (PSI) | MAXIMUM TEMPERATURE (F) | Thread Compound | Strainers | Traps | o'lets | 90 deg elbow | 45 deg elbow | Tee | Coatings | Lining | Unions
CW-01 | Cooling Water; Cooling Water Supply; Cooling Water Return; Condenser Water | CW/CWS/CWR | <=2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Press Fit | Press Fit | Johnson Controls VG1000/VG1245 Series: Popular forged brass, stainless steel trim.Max Pressure: Minimum 150 psi or 250 psi | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket | 8 ft | 225 psig |  | 150 psig | 125 deg F
CW-01 | Cooling Water; Cooling Water Supply; Cooling Water Return; Condenser Water | CW/CWS/CWR | >2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Victallic | Victaulic | 150# Butterfly valves (Lug or Wafer style) or OS&Y Gate valves. Double Regulating Valves (DRV) or Venturi Valves | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket |  | 225 psig |  | 150 psig | 125 deg F
TW-01 | Tower Water; Tower Water Supply; Tower Water Return | TW/TWS/TWR | <=2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Press Fit | Press Fit | Johnson Controls VG1000/VG1245 Series: Popular forged brass, stainless steel trim.Max Pressure: Minimum 150 psi or 250 psi | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket | 8 ft | 225 psig |  | 150 psig | 125 deg F
TW-01 | Tower Water; Tower Water Supply; Tower Water Return | TW/TWS/TWR | >2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Victallic | Victaulic | 150# Butterfly valves (Lug or Wafer style) or OS&Y Gate valves. Double Regulating Valves (DRV) or Venturi Valves | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket |  | 225 psig |  | 150 psig | 125 deg F
TW-01 | Tower Water; Tower Water Supply; Tower Water Return | TW/TWS/TWR | <=2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Press Fit | Press Fit | Johnson Controls VG1000/VG1245 Series: Popular forged brass, stainless steel trim.Max Pressure: Minimum 150 psi or 250 psi | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket | 8 ft | 225 psig |  | 150 psig | 125 deg F
TW-01 | Tower Water; Tower Water Supply; Tower Water Return | TW/TWS/TWR | >2" | Carbon Steel ,ASTM A-234 (forged) or ASTM A-53 (fabricated from pipe). | Sch 40 | ASTM A-536. | Victallic | Victaulic | 150# Butterfly valves (Lug or Wafer style) or OS&Y Gate valves. Double Regulating Valves (DRV) or Venturi Valves | 150# Victallic Style 741 Flange Adapter or Style 7788 Grooved Flange or equal | Couplings 78X5 Victaullic Bolts -Flanges ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Grade E (EPDM - Green Stripe): The most common option for water. Best for hot and cold water, dilute acids, and oil-free air. (Temperature range: -30 to 230° F). [1, 2, 3] | 2" Mineral wool w/ Alum.Jacket |  | 225 psig |  | 150 psig | 125 deg F
REF-01 | Refrigeration Liquid; Suction; Hot Gas | REF | <=2" | 1/4"-2" ASTM B88 TYPE K, SOFT DRAWN BUIRED, ASTM B88 TYPE L, HARD DRAWN (EXPOSED) NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F | [6 empty] | Y
REF-01 | Refrigeration Liquid; Suction; Hot Gas | REF | >2" | 2"&3" - ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F | [6 empty] | Y
VAC-01 | Vacuum; Process Vacuum; Vacuum Air | VAC | <=2" | 304L SS | 10S |  | BW | Weld | Ball | 150# |  |  |  | PTFE | None |  | Vacuum |  | 15 | 300 |  |  |  | Y | Y | Y | Y
VAC-01 | Vacuum; Process Vacuum; Vacuum Air | VAC | >2" | 304L SS | 10S |  | BW | Weld | Ball | 150# |  |  |  | PTFE | None |  | Vacuum |  | 15 | 300 |  |  |  | Y | Y | Y | Y
VEX-01 | Vacuum Pump Exhaust | VEX | <=2" | 304L SS | 10S |  | BW | Weld | Butterfly | [5 empty] | None |  |  |  | 15 | 300 |  |  |  | Y | Y | Y | Y
VEX-01 | Vacuum Pump Exhaust | VEX | >2" | 304L SS | 10S |  | BW | Weld | Butterfly | [5 empty] | None |  |  |  | 15 | 300 |  |  |  | Y | Y | Y | Y
NGAS-01 | Nitrogen; CO2; Oxygen; Argon; Helium; Hydrogen, | NGAS | <=2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | ANSI B16.11, ASTM A105 CLASS 3000 STEEL | ANSI B1.20.1 TAPER THREADED(4) | BALL ≤2 1000 PSI THREE PIECE, FULL PORT, BLOW-OFF PROOF STEMSOCKET WELD OR THREADED CARBON STEEL. CHECK 1/2 TO 2 1000 PSI CWP LIFT CHECK THREADED ALL BRONZE .EQUIPMENT SERVICE REGULATORS(1) GLOBE OR ANGLE ≤1 125 INLET, 2.2 MAX OUTLET DIRECT OPERATED, SPRING LOADED, INTERNAL RELIEF THREADED CAST IRON BODY, ALUMINUM ORIFICE, NITRILE O-RINGS NITRILE O-RINGS | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F |  |  |  | Y | Y | Y | Y
NGAS-01 | Nitrogen; CO2; Oxygen; Argon; Helium; Hydrogen | NGAS | >2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL or SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | PLUG >2 200 CWP LUBRICATED FLANGED CAST IRON BODY, TEFLON COATED PLUG. | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F |  |  |  | Y | Y | Y | Y
FGAS-01 | Propane; LPG; LNG | FGAS | <=2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | ANSI B16.11, ASTM A105 CLASS 3000 STEEL | ANSI B1.20.1 TAPER THREADED(4) | BALL ≤2 1000 PSI THREE PIECE, FULL PORT, BLOW-OFF PROOF STEMSOCKET WELD OR THREADED CARBON STEEL. CHECK 1/2 TO 2 1000 PSI CWP LIFT CHECK THREADED ALL BRONZE .EQUIPMENT SERVICE REGULATORS(1) GLOBE OR ANGLE ≤1 125 INLET, 2.2 MAX OUTLET DIRECT OPERATED, SPRING LOADED, INTERNAL RELIEF THREADED CAST IRON BODY, ALUMINUM ORIFICE, NITRILE O-RINGS NITRILE O-RINGS | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
FGAS-01 | Propane; LPG; LNG | FGAS | >2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL or SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | PLUG >2 200 CWP LUBRICATED FLANGED CAST IRON BODY, TEFLON COATED PLUG. | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
AMM-01 | Ammonia | AMM | <=2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | ANSI B16.11, ASTM A105 CLASS 3000 STEEL | ANSI B1.20.1 TAPER THREADED(4) | BALL ≤2 1000 PSI THREE PIECE, FULL PORT, BLOW-OFF PROOF STEMSOCKET WELD OR THREADED CARBON STEEL. CHECK 1/2 TO 2 1000 PSI CWP LIFT CHECK THREADED ALL BRONZE .EQUIPMENT SERVICE REGULATORS(1) GLOBE OR ANGLE ≤1 125 INLET, 2.2 MAX OUTLET DIRECT OPERATED, SPRING LOADED, INTERNAL RELIEF THREADED CAST IRON BODY, ALUMINUM ORIFICE, NITRILE O-RINGS NITRILE O-RINGS | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
AMM-01 | Ammonia | AMM | >2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL or SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | PLUG >2 200 CWP LUBRICATED FLANGED CAST IRON BODY, TEFLON COATED PLUG. | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
IG-01 | Instrument Gas | IG | <=2" | Tubing SMLS or Welded ASTM-270 | OD | Tri- Clamps or Buttwelded | Ferrules w/ TC or TC x BE | Ferrules w/ TC or TC x BE | Sanitary ball valve, 150# forged 316L stainless steel body sanitary TC x TC. Poppet type check valve, 316L SS, sanitary clamp ends, PTFE TCxTC poppet and gasket. Internal finish 20 Ra max. PBM Model VC or HC or approved equal |  |  | Tri-Clamp, 2 piece heavy duty, 304 stainless steel material hand tightened wing nut type. Tri-Clover Type 13MHHM or approved |  | Molded one piece “O” Ring Gasket. For fractional fittings FDA approved. Tri-Clover 42 MP-E, or approved equal. |  |  | 187.5 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length | 150 psig | 125 deg F
IG-01 | Instrument Gas | IG | >2" | Tubing SMLS or Welded ASTM-270 | OD | Tri- Clamps or Buttwelded | Ferrules w/ TC or TC x BE | Ferrules w/ TC or TC x BE | Tri-clamp ends. Internal finish to be same as tubing (20Ra Max) meeting BPE surface designation SF1. Body to be standard satin finish on exterior. Valves to have TEF seats and seals, stainless steel ball and stem, lockable handle,PBM Igenix Series 8 valves or approved equal stainless steel nuts and bolts. |  |  | Tri-Clamp 2-piece, 304 S.S. high pressure, high temperature (For use above |  | Molded one piece “O” Ring Gasket, FDA approved. Tri-Clover Type 1, 40 MP-E, or equal |  |  | 187.5 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length | 150 psig | 125 deg F
BA-01 | Breathing Air | BA | <=2" | Tubing SMLS or Welded ASTM-270 | OD | Tri- Clamps or Buttwelded | Ferrules w/ TC or TC x BE | Ferrules w/ TC or TC x BE | Sanitary ball valve, 150# forged 316L stainless steel body sanitary TC x TC. Poppet type check valve, 316L SS, sanitary clamp ends, PTFE TCxTC poppet and gasket. Internal finish 20 Ra max. PBM Model VC or HC or approved equal |  |  | Tri-Clamp, 2 piece heavy duty, 304 stainless steel material hand tightened wing nut type. Tri-Clover Type 13MHHM or approved |  | Molded one piece “O” Ring Gasket. For fractional fittings FDA approved. Tri-Clover 42 MP-E, or approved equal. |  |  | 187.5 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length | 150 psig | 125 deg F
BA-01 | Breathing Air | BA | >2" | Tubing SMLS or Welded ASTM-270 | OD | Tri- Clamps or Buttwelded | Ferrules w/ TC or TC x BE | Ferrules w/ TC or TC x BE | Tri-clamp ends. Internal finish to be same as tubing (20Ra Max) meeting BPE surface designation SF1. Body to be standard satin finish on exterior. Valves to have TEF seats and seals, stainless steel ball and stem, lockable handle,PBM Igenix Series 8 valves or approved equal stainless steel nuts and bolts. |  |  | Tri-Clamp 2-piece, 304 S.S. high pressure, high temperature (For use above |  | Molded one piece “O” Ring Gasket, FDA approved. Tri-Clover Type 1, 40 MP-E, or equal |  |  | 187.5 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length | 150 psig | 125 deg F
SA-01 | Service Air | SA | <=2" | ASTM B241,ALUMINUM-ALLOY , SEAMLESS PIPE | STD | Push | Std | Push | Ball | [7 empty] | 150 |  | 150 | 150
SA-01 | Service Air | SA | >2" | ASTM B241,ALUMINUM-ALLOY , SEAMLESS PIPE | STD | Push | Std | Push | Ball | [7 empty] | 150 |  | 150 | 150
DCW-01 | Domestic Cold Water | DCW | <=2" | 1/4"-2" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED) NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
DCW-01 | Domestic Cold Water | DCW | >2" | 2"&3" - ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
DHW-01 | Domestic Hot Water; Domestic Hot Water Return | DHW | <=2" | 1/4"-2" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED) NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
DHW-01 | Domestic Hot Water; Domestic Hot Water Return | DHW | >2" | 2"&3" - ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
RO-01 | RO Feed; RO Water; RO Reject | RO | <=2" | PVC ASTM D2846 CPVC SDR 11/ SS |  | Solvent | PVC | SW | Ball |  |  |  |  | EPDM |  |  | 100 |  | 100 | 140 |  |  |  | Y | Y | Y | Y
RO-01 | RO Feed; RO Water; RO Reject | RO | >2" | PVC ASTM D2846 CPVC SDR 11/SS |  | Solvent | PVC | SW | Ball |  |  |  |  | EPDM |  |  | 100 |  | 100 | 140 |  |  |  | Y | Y | Y | Y
SW-01 | Soft Water | SW | <=2" | ASTM D2846 CPVC SDR 11 | Sch 80 | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | ASTM D2846 CPVC SDR 11 Solvent Cement | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED. CHECK VALVE 1/2 TO 2 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROLTHREADED OR SOLDER BRONZE BODY,STAINLESS STEEL DISC | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1/2" THICK FOR 1" AND SMALLER,1" FOR 1 1/2" AND LARGER,EXTERIOR: PROVIDE ALUMINUM JACKET,INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  | 150 psig | 125 deg F
SW-01 | Soft Water | SW | >2" | ASTM F441 CPVC | Sch 80 | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | ASTMF439 CPVC SCH 80 SOLVENT CEMENT | GATE,GLOBE,BALL,BUTTERFLY,CHECK-CLASS150 CPVC SLIP FIT CONNECTION NSF61 RATED | CPVC 150# | ASTM A-193 (Grade B7) and nuts to ASTM A-194 (Grade 2H). |  |  | Red Rubber | FIBERGLASS INSULATION WITH ASJ,1" FOR 2" AND LARGER, EXTERIOR: PROVIDE ALUMINUM JACKET, INTERIOR: PROVIDE ALUMINUM JACKET, BETWEEN 0'-0" TO 6'-0" AFF. |  | 150 psig |  | 150 psig | 125 deg F
PWP-01 | Process Water | PWP | <=2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEELor PVC ASTM D2846 CPVC SDR 11 | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | Red Rubber |  |  | 225 psig |  | 150 psig | 125 deg F
PWP-01 | Process Water | PWP | >2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL or PVC ASTM D2846 CPVC SDR 11 | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | Red Rubber |  |  | 225psig |  | 150 psig | 125 deg F
BFW-01 | Boiler Feed Water | BFW | <=2" | ANSI B36.10,A106, GRB, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | Red Rubber |  |  | 225 psig |  | 150 psig | 125 deg F
BFW-01 | Boiler Feed Water | BFW | >2" | ANSI B36.10, ASTM 106 GRB , GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | Red Rubber |  |  | 225psig |  | 150 psig | 125 deg F
BBD-01 | Boiler Blowdown | BBD | <=2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3) | ANSI B16.11, ASTM A105 CLASS 3000 | ANSI B1.20.1 TAPER THREADED(3) | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, MEDIUM PRESSURE: SPIRAL WOUND 300 LB GASKET .SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800 |  |  |  | Y | Y | Y | Y
BBD-01 | Boiler Blowdown | BBD | >2" | ASTM A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, HIGH PRESSURE: SPIRAL WOUND 600 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800 |  |  |  | Y | Y | Y | Y
COND-01 | Condensate Return; Condensate Drain | COND | <=2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3) | ANSI B16.11, ASTM A105 CLASS 3000 | ANSI B1.20.1 TAPER THREADED(3) | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, MEDIUM PRESSURE: SPIRAL WOUND 300 LB GASKET .SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800 |  |  |  | Y | Y | Y | Y
COND-01 | Condensate Return; Condensate Drain | COND | >2" | ASTM A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, HIGH PRESSURE: SPIRAL WOUND 600 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800 |  |  |  | Y | Y | Y | Y
DM-01 | Demineralized Water | DM | <=2" | 316L/PVDF |  |  |  |  | Diaphragm |  |  |  |  | PTFE |  |  |  | 150 | 180
DM-01 | Demineralized Water | DM | >2" | 316L/PVDF |  |  |  |  | Diaphragm |  |  |  |  | PTFE |  |  |  | 150 | 180
UPW-01 | Ultra Pure Water | UPW | <=2" | PVDF |  | Fusion | PVDF | Fusion | Diaphragm |  |  |  |  | PTFE |  |  |  | 100 | 180
UPW-01 | Ultra Pure Water | UPW | >2" | PVDF |  | Fusion | PVDF | Fusion | Diaphragm |  |  |  |  | PTFE |  |  |  | 100 | 180
PWFI-01 | Purified Water; WFI | PW/WFI | <=2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5 S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball or True Bore-Self Clean ,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
PWFI-01 | Purified Water; WFI | PW/WFI | >2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball True Bore-Self Clean,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
CIP-01 | CIP Supply; CIP Return; COP | CIP | <=2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5 S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball or True Bore-Self Clean ,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
CIP-01 | CIP Supply; CIP Return; COP | CIP | >2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball True Bore-Self Clean,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
CSTM-01 | Clean Steam; Culinary Steam | CSTM | <=2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5 S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball or True Bore-Self Clean ,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
CSTM-01 | Clean Steam; Culinary Steam | CSTM | >2" | Pipe Sch 5s (tube 083 Wall) 316l Ss 32mi Pid ,Pipe Sch 5S (Tube 083 Wall) 316L SS 32MI PID ,Pipe Sch 5S (Tube .109 Wall )316L SS 32MI PID ASTM A270. 304 is the general industry standard for mild acids, water, and most non-acidic foods. 316L (low carbon) is used for high-acid, high-salt, or highly corrosive CIP fluids and CIP &S IP Piping. | Sch 5S | Butt Joint, TC XTC | Beveled Ends, TC XBE,TCX TC | Beveled Ends, TC XBE,TCX TC W/ Ferrules | Ball Valve Self Flushing Ball True Bore-Self Clean,Diaphram,Check &ButterFly -150# TC ends 316L SS | 150# Ring Joint or Lap Joint | ASTM A193 GRADE 8B, CLASS 2 STAINLESS STEEL, HEAVY HEX HEAD MACHINE BOLTS ASTM 194, GRADE 8 STAINLESS STEEL, HEAVY HEX HEAD FINISHED NUTS | Tri ClampsTwo Piece or Three Piece |  | Gasket 150# Rf Ring 1/16" Restruct. Teflon,Gasket Tc Type – Viton Gf600S,Gasket Tc Type – Steam Resistant Viton,Gasket Tc Type – Ptfe,Gasket Tc Type - Tuf-Steel |  |  | 225 psig | Flexicraft Model 3102 or equal. 150#, 250 °F, sanitary type, 316 SS braid reinforced with FDA compliant silicone liner, Tri-clamp ends, 12” length |  | 150 psig | 125 deg F
PSTM-01 | Process Steam | PSTM | <=2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 STEE | Threaded ANSI B16.11, ASTM A105 CLASS 3000 STEE | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PSTM-01 | Process Steam | PSTM | >2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, LOW PRESSURE: SPIRAL WOUND 150 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 225 psig |  | 150 psig | 125 deg F
PDR-01 | Process Drain; Clean Drain | PDR | <=2" | SS/PVC |  |  |  |  | Ball |  |  |  |  | EPDM
PDR-01 | Process Drain; Clean Drain | PDR | >2" | SS/PVC |  |  |  |  | Ball |  |  |  |  | EPDM
OW-01 | Oily Waste | OW | <=2" | CS |  |  |  |  | Ball |  |  |  |  | PTFE
OW-01 | Oily Waste | OW | >2" | CS |  |  |  |  | Ball |  |  |  |  | PTFE
CHEM-DRN-01 | Acid Waste; Caustic Waste; Neutralization Waste; Chemical Drain | CDR | <=2" | CPVC/PVDF |  | SW | CPVC | SW | Ball |  |  |  |  | EPDM
CHEM-DRN-01 | Acid Waste; Caustic Waste; Neutralization Waste; Chemical Drain | CDR | >2" | CPVC/PVDF |  | SW | CPVC | SW | Ball |  |  |  |  | EPDM
SD-01 | Sanitary Sewer above Grade Floor Drain Header | SD | <=2" | Cast Iron |  | NoHub | CI | NoHub |  |  |  | Clamp
SD-01 | Sanitary Sewer above Grade Floor Drain Header | SD | >2" | Cast Iron |  | NoHub | CI | NoHub |  |  |  | Clamp
PIQ CS-02 | Natural Gas | NG | < = 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | ANSI B16.11, ASTM A105 CLASS 3000 STEEL | ANSI B1.20.1 TAPER THREADED(4) | BALL ≤2 1000 PSI THREE PIECE, FULL PORT, BLOW-OFF PROOF STEMSOCKET WELD OR THREADED CARBON STEEL. CHECK 1/2 TO 2 1000 PSI CWP LIFT CHECK THREADED ALL BRONZE .EQUIPMENT SERVICE REGULATORS(1) GLOBE OR ANGLE ≤1 125 INLET, 2.2 MAX OUTLET DIRECT OPERATED, SPRING LOADED, INTERNAL RELIEF THREADED CAST IRON BODY, ALUMINUM ORIFICE, NITRILE O-RINGS NITRILE O-RINGS | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-02 | Natural Gas | NG | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL or SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | PLUG >2 200 CWP LUBRICATED FLANGED CAST IRON BODY, TEFLON COATED PLUG. | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/8-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-04 | STEAM, LOW PRESSURE | STM LP | < = 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 80 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 STEE | Threaded ANSI B16.11, ASTM A105 CLASS 3000 STEE | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SOCKET WELD | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | ANSI B16.21, RING TYPE, 1/16-INCH THICK |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-04 | STEAM, LOW PRESSURE | STMLP | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL; or ASTM A106, SEAMLESS, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, SCHEDULE 40 ASTM A234 STEEL SOCKET WELD: ANSI B16.11, SCHEDULE 40 ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 150, ASTM A105 OR A181 STEEL, RAISED FACE, SLIP ON OR WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, LOW PRESSURE: SPIRAL WOUND 150 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 225 psig |  | 150 psig | 125 deg F
PIQ CS-05 | STEAM, MEDIUM PRESSURE | STM MP | < = 2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3,4) | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | Threaded ANSI B16.11, ASTM A105 CLASS 3000 | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, LOW PRESSURE: SPIRAL WOUND 150 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 450 psig |  | PRESSURE (PSI)(1): 740 655 600 410 | MAXIMUM TEMPERATURE (F): 100 300 500 800
PIQ CS-05 | STEAM, MEDIUM PRESSURE | STM MP | > 2" | ANSI B36.10, ASTM A53, ERW, GRADE B SCHEDULE 40 BLACK STEEL | Sch 40 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 300, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, MEDIUM PRESSURE: SPIRAL WOUND 300 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 450 psig |  | PRESSURE (PSI)(1): 740 655 600 410 | MAXIMUM TEMPERATURE (F): 100 300 500 800 MAXIMUMPRESSURE (PSI)(1): 740 655 600 410
PIQ CS-06 | STEAM, HIGH PRESSURE | STM HP | < = 2" | A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | ANSI B1.20.1 TAPER THREADED(3) | ANSI B16.11, ASTM A105 CLASS 3000 | ANSI B1.20.1 TAPER THREADED(3) | GATE < 2 ½ 800 PSI RISING STEM, HANDWHEEL SOCKET WELD CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, MEDIUM PRESSURE: SPIRAL WOUND 300 LB GASKET .SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800
PIQ CS-06 | STEAM, HIGH PRESSURE | STM HP | > 2" | ASTM A106, ERW, GRADE B SCHEDULE 80 BLACK STEEL | Sch 80 | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | BUTT WELD: ANSI B16.9, ASTM A234 STEEL, SOCKET WELD: ANSI B16.11, ASTM A105 STEEL | BUTT WELD OR SOCKET WELD, THREADED CONNECTIONS NOT PERMITTED | GATE > 3 TO 24 150 PSI - 600 PSI NON-RISING STEM FLANGED CARBON STEEL | ANSI B16.5 CLASS 600, ASTM A105 STEEL, RAISED FACE WELD NECK | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, HIGH PRESSURE: SPIRAL WOUND 600 LB GASKET. SELF CENTERING RING TYPE, 1/8-INCH THICK, SPIRAL WOUND WITH 304 SS WINDING, GRAPHITE FILLER, STAINLESS STEEL CENTERING RING |  |  | 900 psig |  | MAXIMUM PRESSURE (PSI)(1): 1200 1095 1065 825 | MAXIMUM TEMPERATURE (F): 500 600 700 800
PIQ CS-07 | CHEMICAL | CHEMICAL | < = 2" | 1"-4" THERMALOK STYLE: ASTM A5873 CARBON STEEL, SCHEDULE 40 DIMENSIONS, PTFE LINER and 6"-8" THERMALOK STYLE: ASTM A53, GRADE B CARBON STEEL , SCHEDULE 40 DIMENSIONS, PTFE LINER | Sch 40 | NOT AVAILABLE, USE FLANGED CONNECTIONS,AISI 15V24 STEEL (1"-2") OR ASTM A513 STEEL | ANSI B16.5 ASTM A216 GRADE WCB CAST STEEL, OR FABRICATED CARBON STEEL. | FLANGED | Plastic-Lined Plug or Ball Valves,Tight quarter-turn shutoff, Fully encapsulated bodies and internals where the ball or plug component is either solid plastic or heavily coated in a thick layer of PFA or PTFE, ensuring zero fluid-to-metal contact .Lined Check Valves Flanged Features a poppet-type design where every single surface making contact with the line media is covered with a thick protective layer of plastic to eliminate corrosion and fluid trapping | ROTATING FLANGES: ASTM A395 DUCTILE IRON OR ASTM A105 STEEL; ANSI B16.5 CLASS 150, ASTM A105 STEEL | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | STEAM, HIGH PRESSURE: SPIRAL WOUND 600 LB GASKET. Verify with Engineer. Consider No Gasket LINER THEMALOK MECHANICALLY LOCKED ASTM F1545 PTFE. MINIMUM LINER FLANGE FACE THICKNESS: 0.1" |  |  | 225 psig |  | MAXIMUM PRESSURE (PSI)(1): 285 260 200 170 | MAXIMUM TEMPERATURE (F): -20 to 100 200 400 450
PIQ CS-07 | CHEMICAL | CHEMICAL | > 2" | 1"-4" -6"-8" SWAGED STYLE: ASTM A513 ERW C-1010 ALUMINUM KILLED CARBON STEEL WITH CHEMICAL COMPOSTION MEETING ASTM A587, SCHEDULE 40 DIMENSIONS, PTFE LINED DIAMOND PICKED SPIRAL GROOVED INTERIOR | Sch 40 | (3"-4"), TAPPED OR STANDARD VENTED COUPLER OVER BUTT WELDED LINER ,>4" NOT AVAILABLE, USE FLANGED CONNECTIONS | ANSI B16.5 ASTM A216 GRADE WCB CAST STEEL, OR FABRICATED CARBON STEEL. | Flanged or MECHANICALLY COUPLED WITH BUTT WELDED LINER AVAILABLE THROUGH 4". | Plastic-Lined Plug or Ball Valves,Tight quarter-turn shutoff, Fully encapsulated bodies and internals where the ball or plug component is either solid plastic or heavily coated in a thick layer of PFA or PTFE, ensuring zero fluid-to-metal contact .Lined Check Valves Flanged Features a poppet-type design where every single surface making contact with the line media is covered with a thick protective layer of plastic to eliminate corrosion and fluid trapping | SLIP-ON, WELD NECK AND SOCKET WELD FLANGES: ANSI B16.5 CLASS 150, ASTM A105 STEELANSI B16.5 CLASS 150, ASTM A105 STEEL, CHAMFERED THREADED FLANGE OR ROTATING FLANGE(5) | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | No Gasket -SWAGED MECHANICALLY LOCKED ASTM F1545 PTFE. MINIMUM LINER FLANGE FACE THICKNESS: 0.1" |  |  | 225 psig |  | MAXIMUM PRESSURE (PSI)(1): 285 260 200 170 | MAXIMUM TEMPERATURE (F): -20 to 100 200 400 450
PIQ CU-01-PW | POTABLE WATER | PW | < = 2" | 1/4"-2" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED) NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PW | POTABLE WATER | PW | > 2" | 2"&3" - ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-NP | NON-POTABLE WATER | NPW | < = 2" | 1/4"TO 2" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01 NP | NON-POTABLE WATER | NPW | > 2" | 3" ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PA | PLANT AIR | PA | < = 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ CU-01-PA | PLANT AIR | PA | > 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ-CU -01 F0 | FUEL OIL | FO | < = 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED CODE/ASME B31.9 |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ-CU 01 FO | FUEL OIL | FO | > 2" | ASTM B88 TYPE K, SOFT DRAWN (BURIED) ASTM B88 TYPE L, HARD DRAWN (EXPOSED)NSF 61 LABELED AND APPROVED CODE/ASME B31.9 |  |  | ANSI B16.22, ASTM B73 WROUGHT COPPER; or ANSI B16.18, ASTM B62 CAST BRONZE. AWWA C800(6) AND ANSI B16.26 |  | Ball Valve 600 PSI WOG,TWO PIECE, FULL PORT, LEVER HANDLE,THREADED OR SOLDER ,BRONZE BODY, CHROME PLATED BALL, RTPFE SEATS AND BODY,CHECK VALVE 300 PSI LIFT CHECK WITH DASH POT OR SPRING CONTROL THREADED OR SOLDER,BRONZE BODY, STAINLESS STEEL DISC, PRESSURE RELIEF VALVE 3 TO 250 PSI @ -60 TO 406 F O-RING SEAT THREADED OR SOLDER,STAINLES STEEL TRIM |  |  |  | ANSI B32 ALLOY GRADE SN 94, SN 95 or SN 96. SOLDER AND FLUX SHALL CONTAIN LESS THAN 0.2% LEAD. | [5 empty] | 150 psig | 125 deg F
PIQ-HDPE-01 | OIL & Gas | O&G | < = 2" | HDPE ,ASTM F2619 ,Coiled Pipe |  | Socket Fusion Fittings,ASTM D2683 or Electrofusion Fittings ASTM D3261 / ASTM F1055 or Mechanical Fittings ,ASTM F1924 or ASTM F1948 | Socket Fusion Fittings,ASTM D2683 or Electrofusion Fittings ASTM D3261 / ASTM F1055 or Mechanical Fittings ,ASTM F1924 or ASTM F1948 | Socket Fusion Fittings,ASTM D2683 or Electrofusion Fittings ASTM D3261 / ASTM F1055 or Mechanical Fittings ,ASTM F1924 or ASTM F1948 |  | Flanges and Adapters, ASME B16.5 | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | NONE |  |  | Check with Engineer |  | Check with Engineer | Check with Engineer
PIQ-HDPE-01 | OIL & Gas | O&G | > 2" | HDPE ,ASTM F2619, Pipes > 2" are shipped in straight 40-foot or 50-foot "sticks, |  | Butt Fusion Fittings: Governed by ASTM D3261 or Fabricated Fittings: Governed by ASTM F2206 | Butt Fusion Fittings: Governed by ASTM D3261 or Fabricated Fittings: Governed by ASTM F2206 | Butt Fusion Fittings: Governed by ASTM D3261 or Fabricated Fittings: Governed by ASTM F2206 |  | Flange Adapters & MJ Adapters, ASME B16.5 | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | NONE |  |  | Check with Engineer |  | Check with Engineer | Check with Engineer
PIQ-PE-01 | OIL & Gas | O&G | < = 2" | PE ,ASTM F2619 |  | Molded Fittings: ASTM D3261 for butt-fusion, saddle, and electrofusion fittings or Socket Fittings: ASTM D2683 for socket-fusion fittings or Mechanical Fittings: ASTM F1924 (plastic mechanical fittings for gas or oil) or ASTM F1948 | Molded Fittings: ASTM D3261 for butt-fusion, saddle, and electrofusion fittings or Socket Fittings: ASTM D2683 for socket-fusion fittings or Mechanical Fittings: ASTM F1924 (plastic mechanical fittings for gas or oil) or ASTM F1948 | Molded Fittings: ASTM D3261 for butt-fusion, saddle, and electrofusion fittings or Socket Fittings: ASTM D2683 for socket-fusion fittings or Mechanical Fittings: ASTM F1924 (plastic mechanical fittings for gas or oil) or ASTM F1948 |  | Flanges and Adapters, ASME B16.5 | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | NONE
PIQ-PE-01 | OIL & Gas | O&G | > 2" | PE ,API 15LE |  | Molded Fittings: ASTM D3261 for butt-fusion, saddle, and electrofusion fittings or Socket Fittings: ASTM D2683 for socket-fusion fittings or Mechanical Fittings: ASTM F1924 (plastic mechanical fittings for gas or oil) or ASTM F1948 | Molded Fittings: ASTM D3261 for butt-fusion, saddle, and electrofusion fittings or Socket Fittings: ASTM D2683 for socket-fusion fittings or Mechanical Fittings: ASTM F1924 (plastic mechanical fittings for gas or oil) or ASTM F1948 | Molded Fittings: ASTM D3261 for butt-fusion, saddle, and electrofusion fittings or Socket Fittings: ASTM D2683 for socket-fusion fittings or Mechanical Fittings: ASTM F1924 (plastic mechanical fittings for gas or oil) or ASTM F1948 |  | Flanges and Adapters, ASME B16.5 | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | NONE
PIQ-RO-01 | Reverse Osmosis | RO | < = 2" | Polypropylene (PP), PVDF (Polyvinylidene Fluoride),Stainless Steel or FRP (Fiberglass Reinforced Plastic) |  |  | Push-to-Connect Fittings: These are the standard for lines up to 1/2". Socket Fusion (Heat Welding): For rigid plastic pipes from \(\frac{1}{2}\)" up to 2" (such as Polypropylene or PVDF), Compression Fittings: Plastic or stainless steel compression fittings use a ferrule and nut to squeeze the pipe onto an insert. These are common in high-pressure feed lines under 1". Tri-Clamp (Sanitary) Fittings: Used in pharmaceutical and food-grade RO loops. They utilize a silicone or EPDM gasket sandwiched between two flanged pipe ends, secured by a metallic clamp for easy disassembly and cleaning |  |  | Flange Type: Socket Weld or Threaded (Companion) Flanges. | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS | [8 empty] | Threaded connections, PTFE (Teflon) tape is standard
PIQ-RO-01 | Reverse Osmosis | RO | > 2" | Polypropylene, PVDF, Schedule 80 PVC, 316L/Super Duplex SS |  |  | Butt Fusion,Polypropylene, Flanged,PVDF, Schedule 80 PVC, Tri-Clamp 316L/Super Duplex SS |  |  | Flange Type: Slip-On or Weld Neck Flanges | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS
PIQ-RO-02 | Reverse Osmosis | RO | <=2" | Flex. Tubing 1/4" OD TO 3/8" OD, LLDPE tubing or PEX (cross-linked polyethylene) NSF/ANSI to be lead-free, BPA-free, and taste/odor-free. |  |  | Fittings: Push-to-connect
PIQ-SS-01 | Chemicals, Oxygen(-Indusrial Gas), | Chem. O2, | < = 2" | Sch 40S 316L Stainless Steel ASTM A312/ASME SA312. ASME B36.19M |  | Socket Welded Couplings SS ASTM 182 Gr F316L or ASTM A403 WP316L | Socket-weld fittings SS ASTM A182 GR F316L/ASTM A403 WP316L or Butt-weld fittings (with smooth internal transitions. Dual-ferrule compression fittings (for instrumentation tubing under 1/2"). Copper Alloys: ASTM B62 or ASTM B148 | Socket Welded Couplings SS ASTM 182 Gr F316L or ASTM A403 WP316L or CS Buttweld CS Buttweld |  | Gasket Type: Flat, full-face or ring gaskets | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | < 299 psig Gasket Type: Flat, full-face or ring gaskets.Material: PTFE (Polytetrafluoroethylene) or Filled PTFE (e.g., Durlon 9002 or Garlock GYLON Styles 3502/3505). PTFE is highly resistant to ignition and chemical reactions with pure oxygen.300 psig to 1500psig asket Type: Spiral Wound Gaskets (per ASME B16.20). >1500 psig Gasket Type: Solid Metallic Ring-Type Joint (RTJ) or flat metallic washers. The metal must be softer than the flange face so it deforms under bolt load to create a gas-tight, unburnable seal.
PIQ-SS-01 | Chemicals, Oxygen(-Indusrial Gas), | Chem. O2, | > 2" | Lower Presure Sch 40S 316 L Stainless Steel ASTM A312/ASME SA312. ASME B36.19M or Schedule 80, ASTM A106 Grade B High Pressure |  | Butt weld or Flanged for SS and CS | Butt-weld fittings exclusively (to ensure smooth internal flow profiles and avoid particle entrapment areas) Stainless Steel: ASTM A403 WP316L butt-weld fittings or Carbon Steel: ASTM A234 Grade WPB Note: Carbon steel is only permitted if the system design rigidly limits gas velocity (typically under 30 fps / 9.1 m/s) to eliminate particle-impact friction risks. |  |  | Flanged connections are permitted for component tie-ins using specialized oxygen-compatible, non-combustible gaskets (e.g., PTFE or filled fluoroelastomers). ASTM A105 (forged flanges |  |  |  | < 299 psig Gasket Type: Flat, full-face or ring gaskets.Material: PTFE (Polytetrafluoroethylene) or Filled PTFE (e.g., Durlon 9002 or Garlock GYLON Styles 3502/3505). PTFE is highly resistant to ignition and chemical reactions with pure oxygen.300 psig to 1500psig asket Type: Spiral Wound Gaskets (per ASME B16.20). >1500 psig Gasket Type: Solid Metallic Ring-Type Joint (RTJ) or flat metallic washers. The metal must be softer than the flange face so it deforms under bolt load to create a gas-tight, unburnable seal.
PIQ-HF-01 | HF Acid (Hydrofluoric) | HF | < = 2" | Sch 80 , ASTM A106 Gr. B (Seamless), Monel 400 |  | ASTM A106 Gr. B (Seamless), Monel 400 | ASTM A106 Gr. B (Seamless), Monel 400 | ASTM A106 Gr. B (Seamless), Monel 400 |  | A105 Carbon Steel (w/ raised face), Mon | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | PTFE Enveloped, Spiral-wound Monel with PTFE
> 2"
PIQ--NH3-01 | Ammoia(Anhydrous 0 | NH3 | < = 2" | Sch 40 Welde, Sch 80 Threaded ASTM A53 Gr. B, ASTM A106 Gr. B (No Copper/Brass) ASME B31.3 / B31.5 |  | Socket weld ASTM A53 Gr. B, ASTM A106 Gr. B (No Copper/Brass) ASME B31.3 / B31.5 | Socketweld ASTM A53 Gr. B, ASTM A106 Gr. B (No Copper/Brass) ASME B31.3 / B31.5 | Socket weld, ASTM A53 Gr. B, ASTM A106 Gr. B (No Copper/Brass) ASME B31.3 / B31.5 |  | Socketweld A105 or A350 ,ASME B16.5) / Fittings (ASME B16.9) | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | Spiral-wound 304SS/Graphite, Compressed Non-Asbestos
|  |  | > 2" | [10 empty] | Spiral-wound 304SS/Graphite, Compressed Non-Asbestos
PIQ-H2SO4-01 | Sulfuric Acid | H2SO4 | < = 2" | Sch 40S 316L SS (ASTM A312), Alloy 20, or Sch 80 PTFE-lined CS,ASME B31.3. For estimating only check concentration of H2SO4 for pipe material to be used. |  | Buttweld A182-F316L, Alloy 20, or Lined PTFE CS | Buttweld A182-F316L, Alloy 20, or Lined PTFE CS | Buttweld A182-F316L, Alloy 20, or Lined PTFE CS |  | Weldneck A105 or A350 ,ASME B16.5) /Teflon/PTFE-lined Carbon Steel | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | PTFE, Viton (FKM), Spiral-wound 316L/Graphite
|  |  | > 2" | [7 empty] | ASTM A193, GRADE B7 ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX BOLTS, ASTM A194, GRADE 2H ELECTROPLATED ZINC ALLOY STEEL, HEAVY HEX NUTS |  |  | PTFE, Viton (FKM), Spiral-wound 316L/Graphite